| UNITED NATIONS |  | E |
| --- | --- | --- |
|  | Economic and Social Council | Distr. GENERAL TRANS/WP.11/2005/10 2 August 2005 ENGLISH Original: ENGLISH AND FRENCH |

ECONOMIC COMMISSION FOR EUROPE

INLAND TRANSPORT COMMITTEE

Working Party on the Transport of Perishable Foodstuffs

Sixty-first session,

Geneva, 31 October-3 November 2005

Item 9 of the provisional agenda

AGREEMENT ON THE INTERNATIONAL CARRIAGE OF PERISHABLE FOODSTUFFS AND ON THE SPECIAL EQUIPMENT TO BE USED FOR SUCH CARRIAGE (ATP)

# ATP HANDBOOK

# Prepared by the secretariat

1.	The present document is based on the draft handbook prepared for the fifty-ninth session (TRANS/WP.11/2003/11).

2.	Comments are placed with the provisions of the Agreement to which they refer.

3.	Comments do not modify the provisions of the Agreement or of its Annexes but merely make their contents, meaning and scope more precise.

4.	Comments provide a means of applying the provisions of the Agreement and of its Annexes so as to take into account the development of technology and economic requirements. They could also describe certain recommended practices.

5.	Comments contained in the ATP Handbook are not legally binding for Contracting Parties of the ATP. They are, however, important for the interpretation, harmonization and application of the Agreement as they reflect the opinion of the Working Party on the Transport of Perishable Foodstuffs of the Inland Transport Committee of the Economic Commission for Europe (UNECE).

6.	The text below comprises comments to the Agreement itself and the annexes (for the Annex 1 to ATP, see the revised version as adopted by the Working Party at its sixtieth session).

*	*	*

TABLE OF CONTENTS

##### Page

Agreement on the International Carriage of Perishable

Foodstuffs and on the Special Equipment to be Used

for such Carriage (ATP)											5

Annex 1

DEFINITIONS OF AND STANDARDS FOR SPECIAL

EQUIPMENT FOR THE CARRIAGE OF PERISHABLE FOODSTUFFS			15

- Insulated equipment									15

- Refrigerated equipment									15

- Mechanically refrigerated equipment							16

- Heated equipment										16

##### Annex 1, Appendix 1

Provisions relating to the checking of insulated, refrigerated,

mechanically refrigerated or heated equipment for compliance

with standards												17

##### Annex 1, Appendix 2

Methods and procedures for measuring and checking the insulating

capacity and the efficiency of the cooling or heating appliances of special

equipment for the carriage of perishable foodstuffs							21

- Definitions and general principles								21

- Insulating capacity of equipment								22

2.1	Equipment other than liquid-foodstuffs tanks					22

2.2	Liquid-foodstuffs tanks								23

2.3	Provisions common to all types of insulated equipment			25

- Effectiveness of thermal appliances of equipment					26

3.1	Refrigerated equipment								26

3.2	Mechanically refrigerated equipment						28

3.3	Heated equipment									29

4.	Procedure for measuring the effective refrigerating

capacity Wo of a unit when the evaporator is free from frost			29

4.1	General principles									29

4.2	Test method										30

4.3	Test procedure									30

4.4	Test result										33

5.	Checking the insulating capacity of equipment in service				34

5.1	General examination of the equipment						34

5.2	Examination for air-tightness (not applicable to tank equipment)		34

5.3	Decisions										35

6.	Verifying the effectiveness of thermal appliances of equipment in service	35

  - Refrigerated equipment other than equipment with fixed

eutectic accumulators								35

6.2	Mechanically refrigerated equipment						36

6.3	Heated equipment									36

  - Provisions common to refrigerated, mechanically

refrigerated and heated equipment						36

7.	Test reports											37

##### Annex 1, Appendix 3											69

- Form of certificate for insulated, refrigerated, mechanically

refrigerated or heated equipment used for the international

carriage of perishable foodstuffs by land						69

- Certification plate of compliance of the equipment,

as provided for in annex l, appendix l, paragraph 3					71

Annex 1, Appendix 4

## Distinguishing marks to be affixed to special equipment						73

Annex 2

SELECTION OF EQUIPMENT AND TEMPERATURE

CONDITIONS TO BE OBSERVED FOR THE CARRIAGE

OF QUICK (DEEP)-FROZEN AND FROZEN FOODSTUFFS					75

Annex 2, Appendix 1

Monitoring of air temperatures for transport

of perishable foodstuffs quick frozen									77

Annex 2, Appendix 2

Procedure for the sampling and measurement of

temperature for carriage of chilled, frozen and

quick-frozen perishable foodstuffs quick frozen							78

Annex 3

SELECTION OF EQUIPMENT AND TEMPERATURE

CONDITIONS TO BE OBSERVED FOR THE

CARRIAGE OF CHILLED FOODSTUFFS								81

AGREEMENT ON THE INTERNATIONAL CARRIAGE OF PERISHABLE FOODSTUFFS

AND ON THE SPECIAL EQUIPMENT TO BE USED FOR SUCH CARRIAGE (ATP)

THE CONTRACTING PARTIES,

DESIROUS of improving the conditions of preservation of the quality of perishable foodstuffs during their carriage, particularly in international trade,

CONSIDERING that the improvement of those conditions is likely to promote the expansion of trade in perishable foodstuffs,

HAVE AGREED as follows:

Chapter I

SPECIAL TRANSPORT EQUIPMENT

Article 1

For the international carriage of perishable foodstuffs, equipment shall not be designated as "insulated", "refrigerated", "mechanically refrigerated", or "heated" equipment unless it complies with the definitions and standards set forth in annex 1 to this Agreement.

Article 2

The Contracting Parties shall take the measures necessary to ensure that the equipment referred to in article 1 of this Agreement is inspected and tested for compliance with the said standards in conformity with the provisions of annex 1, appendices 1, 2, 3 and 4, to this Agreement.  Each Contracting Party shall recognize the validity of certificates of compliance issued in conformity with annex 1, appendix 1, paragraph 3 to this Agreement by the competent authority of another Contracting Party.  Each Contracting Party may recognize the validity of certificates of compliance issued in conformity with the requirements of annex 1, appendices 1 and 2, to this Agreement by the competent authority of a State not a Contracting Party.

Comment:

The issuing of a certificate of compliance by the competent authorities on the basis of test reports, is referred to in annex 1, appendix 1, paragraph 3, but there is no indication that such reports had to be issued by a testing station in the country of registration of the equipment.

The test reports in accordance with annex 1, appendix 2 are not certificates. To avoid duplication of the test, each Contracting Party should recognize test stations from any Contracting Party, approved by the competent authority of the country concerned.

Contracting Parties may recognize the test reports, issued by testing stations in countries of non-contracting parties and approved by the competent authority of those countries.

Chapter II

USE OF SPECIAL TRANSPORT EQUIPMENT FOR THE INTERNATIONAL

CARRIAGE OF CERTAIN PERISHABLE FOODSTUFFS

Article 3

1.	The provisions of article 4 of this Agreement shall apply to all carriage, whether for hire or reward or for own account, carried out exclusively - subject to the provisions of paragraph 2 of this article - by rail, by road or by a combination of the two, of

- 	quick (deep)-frozen and frozen foodstuffs, and of

- 	foodstuffs referred to in annex 3 to this Agreement even if they are neither quick (deep)-frozen nor frozen,

if the point at which the goods are, or the equipment containing them is, loaded on to a rail or road vehicle and the point at which the goods are, or the equipment containing them is, unloaded from that vehicle are in two different States and the point at which the goods are unloaded is situated in the territory of a Contracting Party.

In the case of carriage entailing one or more sea crossings other than sea crossings as referred to in paragraph 2 of this article, each land journey shall be considered separately.

2.	The provisions of paragraph 1 of this article shall likewise apply to sea crossings of less than 150 km on condition that the goods are shipped in equipment used for the land journey or journeys without transloading of the goods and that such crossings precede or follow one or more land journeys as referred to in paragraph 1 of this article or take place between two such land journeys.

3.	Notwithstanding the provisions of paragraphs 1 and 2 of this article, the Contracting Parties need not apply the provisions of article 4 of this Agreement to the carriage of foodstuffs not intended for human consumption.

Comment:

Except in the case of the sea crossings referred to in article 3, paragraph 2, land/sea/land transport, with or without reloading of the goods at the end of the sea crossing(s) is not subject to the provisions of the Agreement if the land transport operations in question are not in themselves of an international nature.

Article 4

1.	For the carriage of the perishable foodstuffs specified in annexes 2 and 3 to this Agreement, the equipment referred to in article 1 of this Agreement shall be used unless the temperatures to be anticipated throughout carriage render this requirement manifestly unnecessary for the purpose of maintaining the temperature conditions specified in annexes 2 and 3 to this Agreement.  The equipment shall be so selected and used that the temperature conditions prescribed in the said annexes can be complied with throughout carriage.  Furthermore, all appropriate measures shall be taken, more particularly as regards the temperature of the foodstuffs at the time of loading and as regards icing or re-icing during the journey or other necessary operations.  Nevertheless, the provisions of this paragraph shall apply only in so far as they are not incompatible with international undertakings in the matter of international carriage arising for the Contracting Parties by virtue of conventions in force at the time of the entry into force of this Agreement or by virtue of conventions substituted for them.

2.	If during carriage under this Agreement the provisions of paragraph 1 of this article have not been complied with,

(a)	the foodstuffs may not be disposed of in the territory of a Contracting Party after completion of carriage unless the competent authorities of that Contracting Party deem it compatible with the requirements of public health to authorize such disposal and unless such conditions as the authorities may attach to the authorization when granting it are fulfilled; and

(b)	every Contracting Party may, by reason of the requirements of public health or zooprophylaxis and in so far as it is not incompatible with the other international undertakings referred to in the last sentence of paragraph 1 of this article, prohibit the entry of the foodstuffs into its territory or make their entry subject to such conditions as it may determine.

3.	Compliance with the provisions of paragraph 1 of this article shall be required of carriers for hire or reward only in so far as they have undertaken to procure or provide services intended to ensure such compliance and if such compliance depends on the performance of those services.  If other persons, whether individuals or corporate bodies, have undertaken to procure or provide services intended to ensure compliance with the provisions of this Agreement, they shall be required to ensure such compliance in so far as it depends on performance of the services they have undertaken to procure or provide.

4.	During carriage which is subject to the provisions of this Agreement and for which the loading point is situated in the territory of a Contracting Party, responsibility for compliance with the requirements of paragraph 1 of this article shall rest, subject to the provisions of paragraph 3 of this article,

-	in the case of transport for hire or reward, with the person, whether an individual or a corporate body, who is the consignor according to the transport document or, in the absence of a transport document, with the person, whether an individual or a corporate body, who has entered into the contract of carriage with the carrier;

-	in other cases with the person, whether an individual or a corporate body, who performs carriage.

Chapter III

MISCELLANEOUS PROVISIONS

Article 5

The provisions of this Agreement shall not apply to carriage in containers classified as thermal maritime by land without transloading of the goods where such carriage is preceded or followed by a sea crossing other than a sea crossing as referred to in article 3, paragraph 2, of this Agreement.

Comment:

Land transport by container, preceded or followed by one or more sea crossings, other than those referred to in article 3, paragraph 2, is not subject to the provisions of the Agreement.

# Article 6

1.	Each Contracting Party shall take all appropriate measures to ensure observance of the provisions of this Agreement.  The competent administrations of the Contracting Parties shall keep one another informed of the general measures taken for this purpose.

2.	If a Contracting Party discovers a breach committed by a person residing in the territory of another Contracting Party, or imposes a penalty upon such a person, the administration of the first Party shall inform the administration of the other Party of the breach discovered and of the penalty imposed.

# Article 7

The Contracting Parties reserve the right to enter into bilateral or multilateral agreements to the effect that provisions applicable to special equipment and provisions applicable to the temperatures at which certain foodstuffs are required to be maintained during carriage may, more particularly by reason of special climatic conditions, be more stringent than those prescribed in this Agreement.  Such provisions shall apply only to international carriage between Contracting Parties which have concluded bilateral or multilateral agreements as referred to in this article.  Such agreements shall be transmitted to the Secretary-General of the United Nations, who shall communicate them to Contracting Parties to this Agreement which are not signatories of the said agreements.

Article 8

Failure to observe the provisions of this Agreement shall not affect either the existence or the validity of contracts entered into for the performance of carriage.

Chapter IV

FINAL PROVISIONS

Article 9

1.	States members of the Economic Commission for Europe and States admitted to the Commission in a consultative capacity under paragraph 8 of the Commission's terms of reference may become Contracting Parties to this Agreement

(a)	by signing it;

(b)	by ratifying it after signing it subject to ratification; or

(c)	by acceding to it.

2.	States which may participate in certain activities of the Economic Commission for Europe under paragraph 11 of the Commission's terms of reference may become Contracting Parties to this Agreement by acceding thereto after its entry into force.

3.	This Agreement shall be open for signature until 31 May 1971 inclusive.  Thereafter, it shall be open for accession.

4.	Ratification or accession shall be effected by the deposit of an instrument with the Secretary-General of the United Nations.

Comments:

0.9-1  Signature subject to ratification, acceptance or approval

Where the signature is subject to ratification, acceptance or approval, the signature does not establish the consent to be bound. However, it is a means of authentication and expresses the willingness of the signatory state to continue the treaty-making process. The signature qualifies the signatory state to proceed to ratification, acceptance or approval. It also creates an obligation to refrain, in good faith, from acts that would defeat the object and the purpose of the treaty.

0.9-2  Ratification

Ratification defines the international act whereby a state indicates its consent to be bound to a treaty if the parties intended to show their consent by such an act. In the case of bilateral treaties, ratification is usually accomplished by exchanging the requisite instruments, while in the case of multilateral treaties the usual procedure is for the depository to collect the ratifications of all states, keeping all parties informed of the situation. The institution of ratification grants states the necessary time-frame to seek the required approval for the treaty on the domestic level and to enact the necessary legislation to give domestic effect to that treaty.

0.9-3  Accession

"Accession" is the act whereby a state accepts the offer or the opportunity to become a party to a treaty already negotiated and signed by other states. It has the same legal effect as ratification. Accession usually occurs after the treaty has entered into force.

# Article 10

1.	Any State may at the time of signing this Agreement without reservation as to ratification or of depositing its instrument of ratification or accession or at any time thereafter declare by notification addressed to the Secretary-General of the United Nations that the Agreement does not apply to carriage performed in any or in a particular one of its territories situated outside Europe.  If notification as aforesaid is made after the entry into force of the Agreement in respect of the notifying State the Agreement shall, ninety days after the date on which the Secretary-General has received the notification, cease to apply to carriage in the territory or territories named in that notification. New Contracting Parties acceding to ATP as from 30 April 1999 and applying paragraph 1 of this article shall not be entitled to enter any objection to draft amendments in accordance with the procedure provided for in article 18, paragraph 2.

2.	Any State which has made a declaration under paragraph 1 of this article may at any time thereafter declare by notification addressed to the Secretary-General of the United Nations that the Agreement will be applicable to carriage performed in a territory named in the notification made under paragraph 1 of this article and the Agreement shall become applicable to carriage in that territory one hundred and eighty days after the date on which the Secretary-General has received that notification.

Comments:

0.10-1  Notification

The term "notification" refers to a formality through which a State or an international organisation communicates certain facts or events of legal importance. Notification is increasingly resorted to as a means of expressing final consent. Instead of opting for the exchange of documents or deposit, States may be content to notify their consent to the other party or to the depository. However, all other acts and instruments relating to the life of a treaty may also call for notifications.

0.10-2  Declarations

Sometimes States make "declarations" as to their understanding of some matter or as to the interpretation of a particular provision. Unlike reservations, declarations merely clarify the state's position and do not purport to exclude or modify the legal effect of a treaty. Usually, declarations are made at the time of the deposit of the corresponding instrument or at the time of signature.

Article 11

1.	This Agreement shall come into force one year after five of the States referred to in its article 9, paragraph 1, have signed it without reservation as to ratification or have deposited their instruments of ratification or accession.

2.	With respect to any State which ratifies, or accedes to, this Agreement after five States have signed it without reservation as to ratification or have deposited their instruments of ratification or accession, this Agreement shall enter into force one year after the said State has deposited its instrument of ratification or accession.

# Article 12

1.	Any Contracting Party may denounce this Agreement by giving notice of denunciation to the Secretary-General of the United Nations.

2.	The denunciation shall take effect fifteen months after the date on which the Secretary-General received the notice of denunciation.

Article 13

This Agreement shall cease to have effect if the number of Contracting Parties is less than five throughout any period of twelve consecutive months after its entry into force.

# Article 14

1.	Any State may at the time of signing this Agreement without reservation as to ratification or of depositing its instrument of ratification or accession or at any time thereafter declare by notification addressed to the Secretary-General of the United Nations that this Agreement will be applicable to all or any of the territories for the international relations of which that State is responsible.  This Agreement shall be applicable to the territory or territories named in the notification as from the ninetieth day after receipt of the notice by the Secretary-General or, if on that day the Agreement has not yet entered into force, as from its entry into force.

2.	Any State which has made a declaration under paragraph 1 of this article making this Agreement applicable to a territory for whose international relations it is responsible may denounce the Agreement separately in respect of that territory in conformity with article 12 hereof.

# Article 15

1.	Any dispute between two or more Contracting Parties concerning the interpretation or application of this Agreement shall so far as possible be settled by negotiation between them.

2.	Any dispute which is not settled by negotiation shall be submitted to arbitration if any one of the Contracting Parties concerned in the dispute so requests and shall be referred accordingly to one or more arbitrators selected by agreement between those Parties.  If within three months from the date of the request for arbitration, the Parties concerned in the dispute are unable to agree on the selection of an arbitrator or arbitrators, any of those Parties may request the Secretary-General of the United Nations to designate a single arbitrator to whom the dispute shall be referred for decision.

3.	The decision of the arbitrator or arbitrators designated under the preceding paragraph shall be binding on the Contracting Parties concerned in the dispute.

# Article 16

1.	Any State may, at the time of signing, ratifying, or acceding to, this Agreement, declare that it does not consider itself bound by article 15, paragraphs 2 and 3 of this Agreement.  The other Contracting Parties shall not be bound by these paragraphs with respect to any Contracting Party which has entered such a reservation.

2.	Any Contracting Party which has entered a reservation under paragraph 1 of this article may at any time withdraw the reservation by notification addressed to the Secretary-General of the United Nations.

3.	With the exception of the reservation provided for in paragraph 1 of this article, no reservation to this Agreement shall be permitted.

Comment:

0.16-1  Reservation

A reservation is a declaration made by a State by which it purports to exclude or alter the legal effect of certain provisions of the treaty in their application to that state. A reservation enables a State to accept a multilateral treaty as a whole by giving it the possibility not to apply certain provisions with which it does not want to comply. Reservations can be made when the treaty is signed, ratified, accepted, approved or acceded to. Reservations must not be incompatible with the object and the purpose of the treaty. Furthermore, a treaty might prohibit reservations or only allow for certain reservations to be made.

# Article 17

1.	After this Agreement has been in force for three years, any Contracting Party may, by notification addressed to the Secretary-General of the United Nations, request that a conference be convened for the purpose of revising this Agreement.  The Secretary-General shall notify all Contracting Parties of the request and a revision conference shall be convened by the Secretary-General if, within a period of four months from the date of the notification sent by the Secretary-General, not less than one third of the Contracting Parties signify their assent to the request.

2.	If a conference is convened in pursuance of paragraph 1 of this article, the Secretary-General shall so advise all the Contracting Parties and invite them to submit within a period of three months, the proposals which they wish the conference to consider.  The Secretary-General shall circulate the provisional agenda for the conference, together with the text of such proposals, to all Contracting Parties not less than three months before the date on which the conference is to open.

3.	The Secretary-General shall invite to any conference convened in pursuance of this article all the countries referred to in article 9, paragraph 1, of this Agreement, and also the countries which have become Contracting Parties under the said article 9, paragraph 2.

Comment:

0.17-1  Revision

Some treaties provide for a revision additional to an amendment (i.e., Article 109 of the Charter of the United Nations). In that case, the term "revision" refers to an overriding adoption of the treaty to changed circumstances, whereas the term "amendment" refers only to a change of singular provisions.

# Article 18

1.	Any Contracting Party may propose one or more amendments to this Agreement.  The text of any proposed amendment shall be communicated to the Secretary-General of the United Nations, who shall communicate it to all Contracting Parties and bring it to the notice of all the other States referred to in article 9, paragraph 1, of this Agreement.

The Secretary-General may also propose amendments to this Agreement or to its annexes which have been transmitted to him by the Working Party on the Transport of Perishable Foodstuffs of the Inland Transport Committee of the Economic Commission for Europe.

2.	Within a period of six months following the date on which the proposed amendment is communicated by the Secretary-General, any Contracting Party may inform the Secretary-General

(a)	that it has an objection to the amendment proposed, or

(b)	that, although it intends to accept the proposal, the conditions necessary for such acceptance are not yet fulfilled in its country.

3.	If a Contracting Party sends the Secretary-General a communication as provided for in paragraph 2 (b) of this article, it may, so long as it has not notified the Secretary-General of its acceptance, submit an objection to the proposed amendment within a period of nine months following the expiry of the period of six months prescribed in respect of the initial communication.

4.	If an objection to the proposed amendment is stated in accordance with the terms of paragraphs 2 and 3 of this article, the amendment shall be deemed not to have been accepted and shall be of no effect.

5.	If no objection to the proposed amendment has been stated in accordance with paragraphs 2 and 3 of this article, the amendment shall be deemed to have been accepted on the date specified below:

(a)	if no Contracting Party has sent a communication to the Secretary-General in accordance with paragraph 2 (b) of this article, on the expiry of the period of six months referred to in paragraph 2 of this article;

(b)	if at least one Contracting Party has sent a communication to the Secretary-General in accordance with paragraph 2 (b) of this article, on the earlier of the following two dates:

-	the date by which all the Contracting Parties which sent such communications have notified the Secretary-General of their acceptance of the proposed amendment, subject however to the proviso that if all the acceptances were notified before the expiry of the period of six months referred to in paragraph 2 of this article the date shall be the date of expiry of that period;

-	the date of expiry of the period of nine months referred to in paragraph 3 of this article.

6.	Any amendment deemed to be accepted shall enter into force six months after the date on which it was deemed to be accepted.

7.	The Secretary-General shall as soon as possible inform all Contracting Parties whether an objection to the proposed amendment has been stated in accordance with paragraph 2 (a) of this article and whether one or more Contracting Parties have sent him a communication in accordance with paragraph 2 (b) of this article.  If one or more Contracting Parties have sent him such a communication, he shall subsequently inform all the Contracting Parties whether the Contracting Party or Parties which have sent such a communication raise an objection to the proposed amendment or accept it.

8.	Independently of the amendment procedure laid down in paragraphs 1 to 6 of this article, the annexes and appendices to this Agreement may be modified by agreement between the competent administrations of all the Contracting Parties.  If the administration of a Contracting Party has stated that under its national law its agreement is contingent on special authorization or on the approval of a legislative body, the consent of the Contracting Party concerned to the modification of an annex shall not be deemed to have been given until the Contracting Party has notified the Secretary-General that the necessary authorization or approval has been obtained.  The agreement between the competent administrations may provide that, during a transitional period, the old annexes shall remain in force, wholly or in part, concurrently with the new annexes.  The Secretary-General shall specify the date of the entry into force of the new texts resulting from such modifications.

Comments:

0.18-1  Amendment

The term "amendment" refers to the formal alteration of treaty provisions affecting all the parties to the particular agreement. Such alterations must be effected with the same formalities that attended the original formation of the treaty. Many multilateral treaties lay down specific requirements to be satisfied for amendments to be adopted. In the absence of such provisions, amendments require the consent of all the Parties.

0.18-2  Correction of errors

If, after the authentication of a text, the signatory and Contracting States are agreed that it contains an error, it can be corrected by initialling the corrected treaty text, by executing or exchanging an instrument containing the correction or by executing the corrected text of the whole treaty by the same procedure as in the case of the original text. If there is a depository, the depository must communicate the proposed corrections to all signatory and contracting states. In the UN practice, the Secretary-General, in his function as depository, informs all Parties to a treaty of the errors and the proposal to correct it. If, on the expiry of an appropriate time-limit, no objections are raised by the signatory and Contracting States, the depository circulates a process-verbal of rectification and causes the corrections to be effected in the authentic text(s).

Article 19

In addition to communicating to them the notifications provided for in articles 17 and 18 of this Agreement, the Secretary-General of the United Nations shall notify the States referred to in article 9, paragraph 1, of this Agreement and the States which have become Contracting Parties under article 9, paragraph 2, of:

(a)	signatures, ratifications and accessions under article 9;

(b)	the dates of entry into force of this Agreement pursuant to article 11;

(c)	denunciations under article 12;

(d)	the termination of this Agreement under article 13;

(e)	notifications received under articles 10 and 14;

(f)	declarations and notifications received under article 16, paragraphs 1 and 2;

(g)	the entry into force of any amendment pursuant to article 18.

# Article 20

After 31 May 1971, the original of this Agreement shall be deposited with the Secretary-General of the United Nations, who shall transmit certified true copies to each of the States mentioned in article 9, paragraphs 1 and 2, of this Agreement.

IN WITNESS WHEREOF, the undersigned, being duly authorized thereto, have signed this Agreement.

DONE at Geneva, this first day of September, one thousand nine hundred and seventy, in a single copy, in the English, French and Russian languages, the three texts being equally authentic.

Annex l

DEFINITIONS OF AND STANDARDS FOR SPECIAL EQUIPMENT

FOR THE CARRIAGE OF PERISHABLE FOODSTUFFS

1.	Insulated equipment.  Equipment of which the body 2 is built with insulating walls, doors, floor and roof, by which heat exchanges between the inside and outside of the body can be so limited that the overall coefficient of heat transfer (K coefficient), is such that the equipment is assignable to one or other of the following two categories:

IN   =Normally insulated equipment				-	specified by a K coefficient equal to or less than 0.70 W/m2.K;

IR   =	Heavily insulated equipment

specified by: 						-	a K coefficient equal to or less than 0.40 W/m2.K and by

-	side-walls with a thickness of at least 45 mm for transport equipment of a width greater than 2.50 m.

The definition of the K coefficient and a description of the method to be used in measuring it, are given in appendix 2 to this annex.

2.	Refrigerated equipment.  Insulated equipment which, using a source of cold (natural ice, with or without the addition of salt; eutectic plates; dry ice, with or without sublimation control; liquefied gases, with or without evaporation control, etc.) other than a mechanical or "absorption" unit, is capable, with a mean outside temperature of + 30 °C, of lowering the temperature inside the empty body to, and thereafter maintaining it:

At	+ 7 °C	maximum in the case of class A;

At 	- 10 °C	maximum in the case of class B;

At	- 20 °C	maximum in the case of class C; and

At	   0 °C		maximum in the case of class D.

If such equipment includes one or more compartments, receptacles or tanks for the refrigerant. The said compartments, receptacles or tanks shall:

Be capable of being filled or refilled from the outside; and

Have a capacity in conformity with the provisions of annex l, appendix 2, paragraph 3.1.3.

The K coefficient of refrigerated equipment of classes B and C shall in every case be equal to or less than 0.40 W/m2.K.

3.	Mechanically refrigerated equipment.  Insulated equipment either fitted with its own refrigerating appliance, or served jointly with other units of transport equipment by such an appliance, (fitted with either a mechanical compressor, or an "absorption" device, etc.).  The appliance shall be capable, with a mean outside temperature of + 30 °C, of lowering the temperature Ti inside the empty body to, and thereafter maintaining it continuously in the following manner at:

In the case of classes A, B and C, any desired practically constant inside temperature Ti in conformity with the standards defined below for the three classes:

Class A.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti may be chosen between + 12 °C and 0 °C inclusive;

Class B.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti   may be chosen between + 12 °C and - 10 °C inclusive;

Class C.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti may be chosen between + 12 °C and - 20 °C inclusive.

In the case of classes D, E and F a fixed practically constant inside temperature Ti in conformity with the standards defined below for the three classes:

Class D.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti is equal to or less than 0 °C;

Class E.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti is equal to or less than - 10 °C;

Class F.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti is equal to or less than - 20 °C.  The K coefficient of equipment of classes B, C, E and F shall in every case be equal to or less than 0.40 W/m2.K.

4.	Heated equipment.  Insulated equipment, which is capable of raising the inside temperature of the empty body to, and thereafter maintaining it for not less than 12 hours without renewal of supply at, a practically constant value of not less than + 12 °C when the mean outside temperature, as indicated below:

-10 °C in the case of class A heated equipment;

-20 °C in the case of class B heated equipment.

Heat producing appliances shall have a capacity in conformity with the provisions of annex 1, appendix 2, paragraphs 3.3.1 to 3.3.5.

The K coefficient of equipment of class B shall in every case be equal to or less than 0.40 W/m2.K.

# Annex 1, Appendix 1

PROVISIONS RELATING TO THE CHECKING OF INSULATED, REFRIGERATED, MECHANICALLY REFRIGERATED OR HEATED EQUIPMENT

FOR COMPLIANCE WITH THE STANDARDS

1.	Checks for conformity with the standards prescribed in this annex shall be made:

(a)	before equipment enters into service;

(b)	periodically, at least once every six years;

(c)	whenever required by the competent authority.

Except in the cases provided for in appendix 2, sections 5 and 6, to this annex, the checks shall be made at a testing station designated or approved by the competent authority of the country in which the equipment is registered or recorded, unless, in the case of the check referred to in (a) above, a check has already been made on the equipment itself or on its prototype in a testing station designated or approved by the competent authority of the country in which the equipment was manufactured.

2. 	The methods and procedures to be used in checking for compliance with the standards are described in appendix 2 to this annex.

3. 		A certificate of compliance with the standards shall be issued by the competent authority of the country in which the equipment is to be registered or recorded.  This certificate shall conform to the model reproduced in appendix 3 to this annex.

The certificate of compliance, or a certified true photographic copy thereof, shall be carried on the equipment during carriage to be produced whenever so required by control authorities.  However, if a certification plate, as reproduced in appendix 3 to this annex, is fixed to the equipment, the certification plate of compliance shall be recognized as equivalent to a certificate of compliance.  Certification plates of compliance shall be removed as soon as the equipment ceases to conform to the standards laid down in this annex.

In the case of equipment transferred to another country, which is a Contracting Party to ATP, it shall be accompanied by the following documents so that the competent authority of the country in which the equipment is to be registered or recorded can issue a certificate of compliance:

(a)	in all cases, the test report - of the equipment itself or, in the case of serially produced equipment, of the reference equipment;

(b)	in all cases, the certificate of compliance issued by the competent authority of the country of manufacture or, for equipment in service, the competent authority of the country of registration.  This certificate will be treated as a provisional certificate valid, if necessary, for three months;

(c)	in the case of serially produced equipment, the technical specification of the equipment to be certified (this specification must cover the same items as the descriptive pages concerning the equipment which appears in the test report).

In the case of equipment transferred after it has been in use, the equipment may be subject to a visual inspection to confirm its identity before the competent authority of the country, in which it is to be registered or recorded, issues a certificate of compliance.

Comments to paragraph 3 (c):

While the model ATP certificate is clearly defined in this paragraph, the applications for approval differ from one country to another.  It would therefore be useful for a single format to be proposed for all Contracting Parties.

The test report could be drawn up in the national language of the country, issuing the document. It which should also be drawn up in at least one of the three official languages of ATP.

4.	Distinguishing marks and particulars shall be affixed to the equipment in conformity with the provisions of appendix 4 to this annex.  They shall be removed as soon as the equipment ceases to conform to the standards laid down in this annex.

5. 	The insulated bodies of "insulated", "refrigerated", "mechanically refrigerated" or "heated" transport equipment and their thermal appliances shall each bear permanent distinguishing marks affixed by the manufacturer and including at least the following particulars:

Country of manufacture or letters used in international road traffic;

Name of manufacturer or company;

Model (figures and/or letters);

Serial number;

Month and year of manufacture.

6. 	(a)	New equipment of a specific type serially produced may be approved by testing one unit of that type.  If the unit tested meets class specification, the resulting test report shall be regarded as a Type Approval Certificate.  This certificate shall expire at the end of a period of six years beginning from the date of completion of the test.

The date of expiry of test reports shall be stated in months and years.

Comments to paragraph 6 (a):

A test report is valid for six years as from the date of the finalisation of the test.

(b)	The competent authority shall take steps to verify that production of other units is in conformity with the approved type.  For this purpose it may check by testing sample units drawn at random from the production series.

(c)	A unit shall not be regarded as being of the same type as the unit tested unless it satisfies the following minimum conditions:

(i)	If it is insulated equipment, in which case the reference equipment may be insulated, refrigerated, mechanically refrigerated or heated equipment,

the construction shall be comparable and, in particular, the insulating material and the method of insulation shall be identical;

the thickness of the insulating material shall be not less than that of the reference equipment;

the interior fittings shall be identical or simplified;

the number of doors and the number of hatches or other openings shall be the same or less; and

the inside surface area of the body shall not be as much as 20% greater or smaller;

(ii)	If it is refrigerated equipment, in which case the reference equipment shall be refrigerated equipment,

the conditions set out under (i) above shall be satisfied;

inside circulating fans shall be comparable;

the source of cold shall be identical; and

the reserve of cold per unit of inside surface area shall be greater or equal;

(iii)	If it is mechanically refrigerated equipment, in which case the reference equipment shall be either:

(a)	mechanically refrigerated equipment;

-	the conditions set out in (i) above shall be satisfied; and

-	the effective refrigerating capacity of the mechanical refrigeration appliance per unit of inside surface area, under the same temperature conditions, shall be greater or equal;

or	(b)	insulated equipment to which is complete in every detail but minus its mechanical refrigeration unit which will be fitted at a later date.

The resulting aperture will be filled, during the measurement of the K coefficient, with close fitting panels of the same overall thickness and type of insulation as is fitted to the front wall.  In which case:

-	the conditions set out in (i) above shall be satisfied; and

-	the effective refrigerating capacity of the mechanical refrigeration unit fitted to insulated reference equipment shall be as defined in annex 1, appendix 2, paragraph 3.2.6.

(iv)	If it is heated equipment, in which case the reference equipment may be insulated or heated equipment,

-	the conditions set out under (i) above shall be satisfied;

-	the source of heat shall be identical; and

-	the capacity of the heating appliance per unit of inside surface area shall be greater or equal.

(d)	Modifications causing a reduction in the volume of the insulating material which are additional to the components stated in the manufacturer’s original type approval test report shall be allowed if they meet the following three conditions:

-	the equivalent volume of accumulated insulating material of all components is less than 1/100th of the total volume of insulating material in the insulated unit;

-	the minimum thickness of the remaining insulating material in terms of the components is 20 mm or more;

-	are fitted by the body manufacturer.

(e)	If, in the course of the six-year period, the production series exceeds 100 units, the competent authority shall determine the percentage of units to be tested.

Comments to paragraph 6 (e):

When determining the percentage of units (bodies) to be tested, the competent authority may take into account the manufacturers procedures and quality assurance systems.

# Annex l, Appendix 2

METHODS AND PROCEDURES FOR MEASURING AND CHECKING THE INSULATING CAPACITY AND THE EFFICIENCY OF THE COOLING OR HEATING APPLIANCES OF SPECIAL EQUIPMENT FOR

THE CARRIAGE OF PERISHABLE FOODSTUFFS

## 1.	DEFINITIONS AND GENERAL PRINCIPLES

1.1	K coefficient.  The overall heat transfer coefficient (K coefficient) of the special equipment is defined by the following formula:

K  =  WS .ΔT

where W is either the heating power or the cooling capacity, as the case may be, required to maintain a constant absolute temperature difference T between the mean inside temperature Ti and the mean outside temperature Te, during continuous operation, when the mean outside temperature Te is constant for a body of mean surface area S.

1.2	The mean surface area S of the body is the geometric mean of the inside surface area Si and the outside surface area Se of the body:

S  =  Si.Se

In determining the two surface areas Si and Se, structural peculiarities and surface irregularities of the body, such as chamfers, wheel-arches and similar features, shall be taken into account and shall be noted under the appropriate heading in test reports; however, if the body is covered with corrugated sheet metal the area considered shall be that of the plane surface occupied, not that of the developed corrugated surface.

Temperature measuring points

1.3	In the case of parallelepipedic bodies, the mean inside temperature of the body (Ti) is the arithmetic mean of the temperatures measured 10 cm from the walls at the following 12 points:

(a)	the eight inside corners of the body; and

(b)	the centres of the four inside faces having the largest area.

If the body is not parallelepipedic, the 12 points of measurements shall be distributed as satisfactorily as possible having regard to the shape of the body.

1.4 	In the case of parallelepipedic bodies, the mean outside temperature of the body (Te) is the arithmetic mean of the temperatures measured 10 cm from the walls at the following 12 points:

(a)	the eight outside corners of the body; and

(b)	the centres of the four outside faces having the largest area.

If the body is not parallelepipedic, the 12 points of measurement shall be distributed as satisfactorily as possible having regard to the shape of the body.

1.5 	The mean temperature of the walls of the body is the arithmetic mean of the mean outside temperature of the body and the mean inside temperature of the body:

Te + Ti2

1.6	Temperature measuring instruments protected against radiation shall be placed inside and outside the body at the points specified in paragraphs 1.3 and 1.4 of this appendix.

Steady state period and duration of test

1.7 	The mean outside temperatures and the mean inside temperatures of the body, taken over a steady period of not less than 12 hours, shall not vary by more than ± 0.3 K, and these temperatures shall not vary by more than ± 1.0 K during the preceding 6 hours.

The difference between the heating power or cooling capacity measured over two periods of not less than 3 hours at the start and at the end of the steady state period, and separated by at least 6 hours, shall be less than 3 %.

The mean values of the temperatures and heating or cooling capacity over at least the last 6 hours of the steady state period will be used in K coefficient calculation.

The mean inside and outside temperatures at the beginning and the end of the calculation period of at least 6 hours shall not differ by more that 0.2 K.

2.	INSULATING CAPACITY OF EQUIPMENT

Procedures for measuring the K coefficient

2.1	Equipment other than liquid-foodstuffs tanks

2.1.1 	K coefficient shall be measured in continuous operation either by the internal cooling method or by the internal heating method. In either case, the empty body shall be placed in an insulated chamber.

Test Method

2.1.2	Where the internal cooling method is used, one or more heat exchangers shall be placed inside the body.  The surface area of these exchangers shall be such that, if a fluid at a temperature not lower than 0 °C */ passes through them, the mean inside temperature of the body remains below + 10 °C when continuous operation has been established.  Where the internal heating method is used, electrical heating appliances (resistors, etc.) shall be used.  The heat exchangers or electrical heating appliances shall be fitted with fans having a delivery rate sufficient to obtain 40 to 70 air charges per hour related to the empty volume of the tested body, and the air distribution around all inside surfaces of the tested body shall be sufficient to ensure that the maximum difference between the temperatures of any 2 of the 12 points specified in paragraph 1.3 of this appendix does not exceed 2 K when continuous operation has been established.

2.1.3 	Heat quantity:	The heat dissipated by the electrical resistance fan heaters shall not exceed a flow of 1W/cm2 and the heater units shall be protected by a casing of low emissivity.

The electrical energy consumption shall be determined with an accuracy of 0.5%.

Test Procedure

2.1.4	Whatever the method employed, the mean temperature of the insulated chamber shall throughout the test be kept uniform, and constant in compliance with paragraph 1.7 of this appendix, to within ± 0.5 K, at a level such that the temperature difference between the inside of the body and the insulated chamber is 25 °C ± 2 K, the average temperature of the walls of the body being maintained at + 20 °C ± 0.5 K.

2.1.5	During the test, whether by the internal cooling method or by the internal heating method, the mass of air in the chamber shall be made to circulate continuously so that its speed of movement of the air 10 cm from the walls is maintained at between l and 2 metres/second.

2.1.6	The appliances for generating and distributing cold or heat and for measuring the quantity of cold or heat exchanged and the heat equivalent of the air-circulating fans shall be started up.  Electrical cable losses between the heat input measuring instrument and the tested body shall be established by a measurement or calculation and subtracted from the total heat input measured.

2.1.7	When continuous operation has been established, the maximum difference between the temperatures at the warmest and at the coldest points on the outside of the body shall not exceed 2 K.

2.1.8	The mean outside temperature and the mean inside temperature of the body shall each be read not less than four times per hour.

2.2	Liquid-foodstuffs tanks

2.2.1	The method described below applies only to single-compartment or multiple-compartment tank equipment intended solely for the carriage of liquid foodstuffs such as milk.  Each compartment of such tanks shall have at least one manhole and one discharge-pipe connecting socket; where there are several compartments they shall be separated from one another by non-insulated vertical partitions.

2.2.2	K coefficients shall be measured in continuous operation by internal heating of the empty tank in an insulated chamber.

Test method

2.2.3	An electrical heating appliance (resistors, etc.) shall be placed inside the tank.  If the tank has several compartments, an electrical heating appliance shall be placed in each compartment.  The electrical heating appliances shall be fitted with fans with a delivery rate sufficient to ensure that the difference between the maximum temperature and the minimum temperature inside each compartment does not exceed 3 K when continuous operation has been established.  If the tank comprises several compartments, the difference between the mean temperature in the coldest compartment and the mean temperature in the warmest compartment shall not exceed 2 K, the temperatures being measured as specified in paragraph 2.2.4 of this appendix.

2.2.4	Temperature measuring instruments protected against radiation shall be placed inside and outside the tank 10 cm from the walls, as follows:

(a)	If the tank has only one compartment, measurements shall be made at a minimum of 12 points positioned as follows:

The four extremities of two diameters at right angles to one another, one horizontal and the other vertical, near each of the two ends of the tank;

The four extremities of two diameters at right angles to one another, inclined at an angle of 45° to the horizontal, in the axial plane of the tank;

(b)	If the tank has several compartments, the points of measurement shall be as follows:

for each of the two end compartments, at least the following:

The extremities of a horizontal diameter near the end and the extremities of a vertical diameter near the partition;

and for each of the other compartments, at least the following:

The extremities of a diameter inclined at an angle of 45° to the horizontal near one of the partitions and the extremities of a diameter perpendicular to the first and near the other partition.

The mean inside temperature and the mean outside temperature of the tank shall respectively be the arithmetic mean of all the measurements taken inside and all the measurements taken outside the tank.  In the case of a tank having several compartments, the mean inside temperature of each compartment shall be the arithmetic mean of the measurements, numbering not less than four, relating to that compartment.

Test procedure

2.2.5	Throughout the test, the mean temperature of the insulated chamber shall be kept uniform, and constant in compliance with paragraph 1.7 of this appendix, at a level such that the difference in temperature between the inside of the tank and that of the insulated chamber is not less than 25 °C ± 2 K, with the average temperature of the tank walls being maintained at + 20 °C ± 0.5 K.

2.2.6	The mass of air in the chamber shall be made to circulate continuously so that the speed of movement of the air 10 cm from the walls is maintained at between l and 2 metres/second.

2.2.7	The appliances for heating and circulating the air and for measuring the quantity of heat exchanged and the heat equivalent of the air-circulating fans shall be started up.

2.2.8	When continuous operation has been established, the maximum difference between the temperatures at the warmest and at the coldest points on the outside of the tank shall not exceed 2 K.

2.2.9	The mean outside temperature and the mean inside temperature of the tank shall each be read not less than four times per hour.

2.3	Provisions common to all types of insulated equipment

2.3.1	Verification of the K coefficient

Where the purpose of the tests is not to determine the K coefficient but simply to verify that it is below a certain limit, the tests carried out as described in paragraphs 2.1.1. to 2.2.9 of this appendix may be stopped as soon as the measurements made show that the K coefficient meets the requirements.

2.3.2	Accuracy of measurements of the K coefficient

Testing stations shall be provided with the equipment and instruments necessary to ensure that the K coefficient is determined with a maximum margin of error of ± 10% when using the method of internal cooling and ± 5% when using the method of internal heating.

Comments to paragraph 2.32:

1.	Examples for the errors which are normally taken into account by the test stations are temperature, power and the surface area of the body.

The method of calculating the error, which is usually applied, is the total admissible error ε:

ε=ΔSS2+ΔWW2+2ΔTTe−Ti

or the absolute error em:

em=ΔSS+ΔWW+2.ΔTTe−Ti

where:

S is the mean surface area of the vehicle body (geometric mean of the internal and external surfaces);

W is the power dissipated inside the vehicle body in the steady state Te and Ti are in the respective external and internal temperatures of the vehicle body under test.

2.	Under normal test conditions, S can be measured to 1% . However, there are cases where it is impossible to measure with this precision.

The error of W does not exceed 1 %, although certain test stations use equipment giving a greater error.

Temperature is measured with an absolute accuracy of  0.1 K. The measurement of a temperature difference (Te - Ti) of the order of 20 K therefore gives an error of twice 0,5 %, i.e. 1%.

The total error is therefore  = 0.017 i.e. 1.7 %. The maximum admissible error is em = 3%.

3.	Other errors which have not been taken into consideration can have an effect on the exact value of the K coefficient. These errors are as follows:

(a)	Latent errors due to admissible variations in the internal and external temperatures, which are a function of the thermal inertia of the walls of the equipment, the temperature and time;

(b)	Errors due to the variation of air velocity at the boundary layer and its effect on the thermal resistance.

If the internal and external air velocities are of equal value, the possible error will be about 2.5 % as between 1 to 2 m/s for a mean K coefficient of 0.40 W/m2.K. For a K coefficient of 0.70 W/m2.K, this error will be nearly 5%.  If there are significant thermal bridges, the influence of the speed and direction of the air will be greater.

4.	Finally, because of the error in the estimation of the surface area of the body, an error which in practice is difficult to calculate when dealing with non standard equipment, (this estimation involving factors of a subjective nature), one could envisage the determination of the error in the measurement of the overall heat transfer per degree temperature difference:

WTe−Ti=K.S

3.	EFFECTIVENESS OF THERMAL APPLIANCES OF EQUIPMENT

### Procedures for determining the efficiency of thermal appliances of equipment

3.1	Refrigerated equipment

3.1.1	The empty equipment shall be placed in an insulated chamber whose mean temperature shall be kept uniform, and constant to within ± 0.5 K, at + 30 °C.  The mass of air in of the chamber shall be made to circulate as described in paragraph 2.1.5 of this appendix.

3.1.2	Temperature measuring instruments protected against radiation shall be placed inside and outside the body at the points specified in paragraphs 1.3 and 1.4 of this appendix.

Test procedure

3.1.3	(a)	In the case of equipment other than equipment with fixed eutectic plates, and equipment fitted with liquefied gas systems, the maximum weight of refrigerant specified by the manufacturer or which can normally be accommodated shall be loaded into the spaces provided when the mean inside temperature of the body has reached the mean outside temperature of the body (+ 30 °C).  Doors, hatches and other openings shall be closed and the inside ventilation appliances (if any) of the equipment shall be started up at maximum capacity.  In addition, in the case of new equipment, a heating appliance with a heating capacity equal to 35% of the heat exchanged through the walls in continuous operation shall be started up inside the body when the temperature prescribed for the class to which the equipment is presumed to belong has been reached.  No additional refrigerant shall be loaded during the test;

(b)	In the case of equipment with fixed eutectic plates, the test shall comprise a preliminary phase of freezing of the eutectic solution.  For this purpose, when the mean inside temperature of the body and the temperature of the plates have reached the mean outside temperature (+ 30 °C), the plate-cooling appliance shall be put into operation for 18 consecutive hours after closure of the doors and hatches.  If the plate-cooling appliance includes a cyclically-operating mechanism, the total duration of operation of the appliance shall be 24 hours.  In the case of new equipment, as soon as the cooling appliance is stopped, a heating appliance with a heating capacity equal to 35% of the heat exchanged through the walls in continuous operation shall be started up inside the body when the temperature prescribed for the class to which the equipment is presumed to belong has been reached.  The solution shall not be subjected to any re-freezing operation during the test;

(c)	In the case of equipment fitted with liquefied gas systems, the following test procedure shall be used:  when the mean inside temperature of the body has reached the mean outside temperature (+ 30 °C), the receptacles for the liquefied gas shall be filled to the level prescribed by the manufacturer.  Then the doors, hatches and other openings shall be closed as in normal operation and the inside ventilation appliances (if any) of the equipment shall be started up at maximum capacity.  The thermostat shall be set at a temperature not more than 2 degrees below the limit temperature of the presumed class of the equipment.  Cooling of the body then shall be commenced.  During the cooling of the body the refrigerant consumed is simultaneously replaced.  This replacement shall be effected:

Either for a time corresponding to the interval between the commencement of cooling and the moment when the temperature prescribed for the class to which the equipment is presumed to belong is reached for the first time; or

For a duration of three hours counting from the commencement of cooling, whichever is shorter.

Beyond this period, no additional refrigerant shall be loaded during the test.

In the case of new equipment, a heating appliance with a heating capacity equal to 35% of the heat exchanged through the walls in continuous operation shall be started up inside the body when the class temperature has been reached.

Provisions common to all types of refrigerated equipment

3.1.4	The mean outside temperature and the mean inside temperature of the body shall each be read not less often than once every 30 minutes.

3.1.5	The test shall be continued for 12 hours after the mean inside temperature of the body has reached the lower limit prescribed for the class to which the equipment is presumed to belong (A  = + 7 °C; B = - 10 °C; C = - 20 °C; D = 0 °C) or, in the case of equipment with fixed eutectic plates, after stoppage of the cooling appliance.

Criterion of satisfaction

3.1.6	The test shall be deemed satisfactory if the mean inside temperature of the body does not exceed the aforesaid lower limit during the aforesaid period of 12 hours.

### 3.2	Mechanically refrigerated equipment

Test method

3.2.1	The test shall be carried out in the conditions described in paragraphs 3.1.1 and 3.1.2 of this appendix.

Test procedure

3.2.2	When the mean inside temperature of the body reaches the outside temperature (+ 30 °C), the doors, hatches and other openings shall be closed and the refrigerating appliance and the inside ventilating appliances (if any) shall be started up at maximum capacity.  In addition, in the case of new equipment, a heating appliance with a heating capacity equal to 35% of the heat exchanged through the walls in continuous operation shall be started up inside the body when the temperature prescribed for the class to which the equipment is presumed to belong has been reached.

3.2.3	The mean outside temperature and the mean inside temperature of the body shall each be read not less often than once every 30 minutes.

3.2.4	The test shall be continued for 12 hours after the mean inside temperature of the body has reached:

Either the lower limit prescribed for the class to which the equipment is presumed to belong in the case of classes A, B and C (A = 0 °C; B = - 10 °C; C = - 20 °C); or

A level not lower than the upper limit prescribed for the class to which the equipment is presumed to belong in the case of classes D, E, and F (D = 0 °C; E = - 10 °C; F = - 20 °C).

Criterion of satisfaction

3.2.5	The test shall be deemed satisfactory if the refrigerating appliance is able to maintain the prescribed temperature conditions during the said 12-hour periods, with any automatic defrosting of the refrigerating unit not being taken into account.

3.2.6	If the refrigerating appliance with all its accessories has undergone separately, to the satisfaction of the competent authority, a test to determine its effective refrigerating capacity at the prescribed reference temperatures, the transport equipment may be accepted as mechanically refrigerated equipment without undergoing an efficiency test if the effective refrigerating capacity of the appliance in continuous operation exceeds the heat loss through the walls for the class under consideration, multiplied by the factor l.75.

Comment to paragraph 3.2.6:

The proposed provision concerning the use of a multiplier factor of 1.75 when determining the refrigerating capacity of the appliance to be installed on a body, is to be applicable whether or not the body was fitted with an appliance when the K coefficient was measured.  If during the insulation test the body was not equipped with an appliance, it would be advisable to ensure that the K coefficient of that body when equipped with an appliance does not exceed the class limits, in order to allow for the variations that might occur with equipment of differing lengths or types.

3.2.7	If the mechanically refrigerating unit is replaced by a unit of a different type, the competent authority may:

(a)	require the equipment to undergo the determinations and verifications prescribed in paragraphs 3.2.1 to 3.2.4; or

(b)	satisfy itself that the effective refrigerating capacity of the new mechanically refrigerating unit is, at the temperature prescribed for equipment of the class concerned, at least equal to that of the unit replaced; or

(c)	satisfy itself that the effective refrigerating capacity of the new mechanically refrigerating unit meets the requirements of paragraph 3.2.6.

### 3.3	Heated equipment

Test method

3.3.1	The empty equipment shall be placed in an insulated chamber whose temperature shall be kept uniform and constant at as low a level as possible.  The atmosphere of the chamber shall be made to circulate as described in paragraph 2.1.5 of this appendix.

3.3.2	Temperature measuring instruments protected against radiation shall be placed inside and outside the body at the points specified in paragraphs 1.3 and 1.4 of this appendix.

Test procedure

3.3.3	Doors, hatches and other openings shall be closed and the heating equipment and the inside ventilating appliances (if any) shall be started up at maximum capacity.

3.3.4	The mean outside temperature and the mean inside temperature of the body shall each be read not less often than once every 30 minutes.

3.3.5	The test shall be continued for 12 hours after the difference between the mean inside temperature and the mean outside temperature of the body has reached the level corresponding to the conditions prescribed for the class to which the equipment is presumed to belong. In the case of new equipment, the above temperature difference shall be increased by 35 per cent.

Criterion of satisfaction

3.3.6	The test shall be deemed satisfactory if the heating appliance is able to maintain the prescribed temperature difference during the 12 hours aforesaid.

4.	Procedure for measuring the effective refrigerating capacity Wo of a unit when the evaporator is free from frost

4.1	General principles

4.1.1	When attached to either a calorimeter box or the insulated body of a unit of transport equipment, and operating continuously, this capacity is:

Wo=Wj + U. T

where U is the heat leakage of the calorimeter box or insulated body, Watts/°C.

T is the difference between the mean inside temperature Ti and the mean outside temperature Te of the calorimeter or insulated body (K),

Wj is the heat dissipated by the fan heater unit to maintain each temperature difference in equilibrium.

4.2	Test method

4.2.1	The refrigeration unit is either fitted to a calorimeter box, or the insulated body of a unit of transport equipment.

In each case, the heat leakage is measured at a single mean wall temperature prior to the capacity test.  An arithmetical correction factor, based upon the experience of the testing station, is made to take into account the average temperature of the walls at each thermal equilibrium during the determination of the effective refrigerating capacity.

It is preferable to use a calibrated calorimeter box to obtain maximum accuracy.

Measurements and procedure shall be as described in paragraphs 1.1 to 2.1.8 above; however, it is sufficient to measure U the heat leakage only, the value of this coefficient being defined by the following relationship:

U=WΔTm

where:

W	is the heating power (in watts) dissipated by the internal heater and fans;

ΔTm	is the difference between the mean internal temperature Ti and the mean external temperature Te;

U	is the heat flow per degree of difference between the air temperature inside and outside the calorimeter box or unit of transport equipment measured with the refrigeration unit fitted.

The calorimeter box or unit of transport equipment is placed in a test chamber.  If a calorimeter box is used, U.ΔT should be not more than 35% of the total heat flow Wo.

The calorimeter box or unit of transport equipment shall be heavily insulated.

Comment to paragraph 4.2.1:

The U factor of a calorimeter box is usually measured without the refrigeration unit fitted to the aperture.  In the case of a unit of transport equipment, measurement of U may be made with or without the refrigeration unit fitted to the insulated body, in the absence of a refrigeration unit an insulated panel is fitted to the aperture.

4.2.2 	Instrumentation

Test stations shall be equipped with instruments to measure the U value to an accuracy of ± 5%.  Heat transfer through air leakage should not exceed 5% of the total heat transfer through the calorimeter box or through the insulated body of the unit of transport equipment. The refrigerating capacity shall be determined with an accuracy of ± 5%.

The instrumentation of the calorimeter box or unit of transport equipment shall conform to paragraphs 4 1.3 and 1.4 above.  The following are to be measured:

(a)	Air temperatures:	At least four thermometers uniformly distributed at the inlet to the evaporator;

At least four thermometers uniformly distributed at the outlet to the evaporator;

At least four thermometers uniformly distributed at the air inlet(s) to the refrigeration unit;

The thermometers shall be protected against radiation.

The accuracy of the temperature measuring system shall be 0.2 K;

(b)	Energy consumption:	Instruments shall be provided to measure the electrical energy or fuel consumption of the refrigeration unit.

The electrical energy and fuel consumption shall be determined with an accuracy of 0.5%;

(c)	Speed of rotation:	Instruments shall be provided to measure the speed of rotation of the compressors and circulating fans or to allow these speeds to be calculated where direct measurement is impractical.

The speed of rotation shall be measured to an accuracy of 1%;

(d)	Pressure:	High precision pressure gauges (accurate to ± 1%) shall be fitted to the condenser and evaporator and to the compressor inlet when the evaporator is fitted with a pressure regulator.

4.2.3 	Test conditions

(i)	The average air temperature at the inlet(s) to the refrigeration unit shall be maintained at 30 °C + 0.5 K.

The maximum difference between the temperatures at the warmest and at the coldest points shall not exceed 2 K.

(ii)	Inside the calorimeter box or the insulated body of the unit of transport equipment (at the air inlet to the evaporator):  there shall be three levels of temperature between -25 °C and +12 °C depending on the characteristics of the unit, one temperature level being at the minimum prescribed for the class requested by the manufacturer with a tolerance of ± 1 K.

The mean inside temperature shall be maintained within a tolerance of ± 0.5 K.  During the measurement of refrigerating capacity, the heat dissipated within the calorimeter box or the insulated body of the unit of transport equipment shall be maintained at a constant level with a tolerance of ± 1%.

When presenting a refrigeration unit for test, the manufacturer shall supply:

-	Documents describing the unit to be tested;

-	A technical document outlining the parameters that are most important to the functioning of the unit and specifying their allowable range;

-	The characteristics of the equipment series tested; and

-	A statement as to which prime mover(s) shall be used during testing.

4.3	Test procedure

4.3.1	The test shall be divided into two major parts, the cooling phase and the measurement of the effective refrigerating capacity at three increasing temperature levels.

(a)	Cooling phase; the initial temperature of the calorimeter box or transport equipment shall be within ± 3 K of the prescribed ambient temperature.  It shall then be lowered by 5 K below the lower limit class temperature;

(b)	Measurement of effective refrigerating capacity, at each internal temperature level.

A first test to be carried out, for at least four hours at each level of temperature, under control of the thermostat (of the refrigeration unit) to stabilize the heat transfer between the interior and exterior of the calorimeter box or unit of transport equipment.

A second test shall be carried out without the thermostat in operation in order to determine the maximum refrigerating capacity, with the heating power of the internal heater producing an equilibrium condition at each temperature level as prescribed in paragraph 4.2.3.

The duration of the second test shall be not less than four hours.

Before changing from one temperature level to another, the box or unit shall be manually defrosted.

If the refrigeration unit can be operated by more than one form of energy, the tests shall be repeated accordingly.

If the compressor is driven by the vehicle engine, the test shall be carried out at both the minimum speed and at the nominal speed of rotation of the compressor as specified by the manufacturer.

If the compressor is driven by the vehicle motion, the test shall be carried out at the nominal speed of rotation of the compressor as specified by the manufacturer.

4.3.2	The same procedure shall be followed for the enthalpy method described below, but in this case the heat power dissipated by the evaporator fans at each temperature level shall also be measured.

This method may, alternatively, be used to test reference equipment. In this case, the effective refrigerating capacity is measured by multiplying the mass flow (m) of the refrigerant liquid by the difference in enthalpy between the refrigerant vapour leaving the unit (ho) and the liquid at the inlet to the unit (hi).

To obtain the effective refrigerating capacity, the heat generated by the evaporator fans (Wf) is deducted.  It is difficult to measure Wf if the evaporator fans are driven by an external motor, in this particular case the enthalpy method is not recommended.  When the fans are driven by internal electric motors, the electrical power is measured by appropriate instruments with an accuracy of ± 3%, with refrigerant flow measurement being accurate to ± 5%.

The heat balance is given by the formula:

Wo = (ho - hi) m - Wf.

Appropriate methods are described in standards ISO 971, BS 3122, DIN, NEN, etc.  An electric heater is placed inside the equipment in order to obtain the thermal equilibrium.

4.3.3	Precautions

As the tests for effective refrigerating capacity are carried out with the thermostat of the refrigeration unit disconnected, the following precautions shall be observed:

if the equipment has a hot gas injection system, it shall be inoperative during the test;

with automatic controls of the refrigeration unit which unload individual cylinders (to tune the capacity of the refrigeration unit to motor output) the test shall be carried out with the number of cylinders appropriate for the temperature.

4.3.4	Checks

The following should be verified and the methods used indicated on the test report:

(i)	the defrosting system and the thermostat are functioning correctly;

(ii)	the rate of air circulation is that specified by the manufacturer.

If the air circulation of a refrigeration unit’s evaporator fans are to be measured, methods capable of measuring the total delivery volume shall be used. Use of one of the relevant existing standards, i.e. BS 848, ISO 5801, AMCA 210-85, DIN 24163, NFE 36101, NF X10.102, DIN 4796 is recommended;

(iii)	the refrigerant used for tests is that specified by the manufacturer.

4.4	Test result

4.4.1	The refrigeration capacity for ATP purposes is that relating to the mean temperature at the inlet(s) of the evaporator.  The temperature measuring instruments shall be protected against radiation.

5.	Checking the insulating capacity of equipment in service

For the purpose of checking the insulating capacity of each piece of equipment in service as prescribed in appendix 1, paragraphs l (b) and 1 (c), to this annex, the competent authorities may:

Apply the methods described in paragraphs 2.1.1 to 2.3.2 of this appendix; or

Appoint experts to assess the fitness of the equipment for retention in one or other of the categories of insulated equipment.  These experts shall take the following particulars into account and shall base their conclusions on information as indicated below.

5.1	General examination of the equipment

This examination shall take the form of an inspection of the equipment to determine the following:

(i)	the general design of the insulating sheathing;

(ii)	the method of application of insulation;

(iii)	the nature and condition of the walls;

(iv)	the condition of the insulated compartment;

(v)	the thickness of the walls;

and to make all appropriate observations concerning the effective insulating capacity of the equipment. For this purpose the experts may cause parts of the equipment to be dismantled and require all documents they may need to consult (plans, test reports, specifications, invoices, etc.) to be placed at their disposal.

Comment to5.1:

Changes in the K-coefficient during the service life of insulated bodies depend on the following factors:

(a)	 Nature of the insulating material;

(b) 	Nature of the covering layers (glass-fibre reinforced plastics or metal);

(c) 		Construction of the body;

(d)		Number of doors and hatches permitted in the approval tests;

(e)		Conditions of use (carriage of fresh produce or frozen or quick (deep) - frozen products).

5.2	Examination for air-tightness (not applicable to tank equipment)

The inspection shall be made by an observer stationed inside the equipment, which shall be placed in a brightly-illuminated area.  Any method yielding more accurate results may be used.

5.3	Decisions

(i)	If the conclusions regarding the general condition of the body are favourable, the equipment may be kept in service as insulated equipment of its initial class for a further period of not more than three years.  If the conclusions of the expert or experts are not acceptable, the equipment may be kept in service only following a satisfactory measurement of K coefficient according to the procedure described in paragraphs 2.1.1 to 2.3.2 of this appendix; it may then be kept in service for a further period of six years.

- In the case of heavily insulated equipment, if the conclusions of an expert or experts show the body to be unsuitable for keeping in service in its initial class but suitable for continuing in service as normally insulated equipment, then the body may be kept in service in an appropriate class for a further three years.  In this case, the distinguishing marks (as in appendix 4 of this annex) shall be changed appropriately.

(iii)	If the equipment consists of units of serially-produced equipment of a particular type satisfying the requirements of appendix l, paragraph 6, to this annex and belonging to one owner, then in addition to an inspection of each unit of equipment the K coefficient of not less than l% of the number of units involved, may be measured in conformity with the provisions of sections 2.1, 2.2 and 2.3 of this appendix.  If the results of the examinations and measurements are acceptable, all the equipment in question may be kept in service as insulating equipment of its initial class for a further period of six years.

Comment to 5.3:

Some countries consider 0.40 to be the maximum K-value for classes B, C, E and F also by re-approval, and others are of the opinion that re-approval is done by fulfilling sections 5 and 6.

Re-approval can be carried out either by a test station ensuring the maximum K-value for classes B,C, E and F is less than 0.40 W/m2.K and 0.70 W/m2.K for classes A and D or by fulfilling sections 5 and 6.

6.	Verifying the EFFECTIVENESS of thermal appliances of equipment in service

To verify as prescribed in appendix l, paragraphs l (b) and l (c), to this annex the effectiveness of the thermal appliance of each item of refrigerated, mechanically refrigerated or heated equipment in service, the competent authorities may:

Apply the methods described in sections 3.1, 3.2 and 3.3 of this appendix; or

Appoint experts to apply the following provisions:

6.1	Refrigerated equipment other than equipment with fixed eutectic accumulators

It shall be verified that the inside temperature of the empty equipment, previously brought to the outside temperature, can be brought to the limit temperature of the class to which the equipment belongs, as prescribed in this annex, and maintained below the said limit temperature for a period t

such that t≥12ΔTΔT'	in which

ΔT is the difference between + 30 °C and the said limit temperature, and

ΔT' is the difference between the mean outside temperature during the test and the class limit temperature, the outside temperature being not lower than + 15 °C.

If the results are acceptable, the equipment may be kept in service as refrigerated equipment of its initial class for a further period of not more than three years.

6.2	Mechanically refrigerated equipment

Checks shall be made to ensure that, when the outside temperature is not lower than + 15 °C, the inside temperature of the empty equipment, which has been previously equalized to that outside, can be reduced to the required class temperature within a maximum period of 6 hours:

In the case of equipment in classes A, B or C, to the minimum temperature, as prescribed in this annex;

In the case of equipment in classes D, E or F, to the limit temperature, as prescribed in this annex.

If the results are acceptable, the equipment may be kept in service as mechanically refrigerated equipment of its initial class for a further period of not more than three years.

6.3	Heated equipment

It shall be verified that the difference between the inside temperature of the equipment and the outside temperature which governs the class to which the equipment belongs as prescribed in this annex (a difference of 22 K in the case of class A and of 32 K in the case of class B) can be achieved and be maintained for not less than 12 hours.  If the results are acceptable, the equipment may be kept in service as heated equipment of its initial class for a further period of not more than three years.

6.4	Provisions common to refrigerated, mechanically refrigerated and heated equipment

(i)	If the results are not acceptable, refrigerated, mechanically refrigerated or heated equipment may be kept in service in its initial class only if it passes at a testing station the tests described in sections 3.1, 3.2 and 3.3 of this appendix; it may then be kept in service in its initial class for a further period of six years.

(ii)	If the equipment consists of units of serially-produced refrigerated, mechanically refrigerated or heated equipment of a particular type satisfying the requirements of appendix l, paragraph 6, to this annex and belonging to one owner, then in addition to an inspection of the thermal appliances to ensure that their general condition appears to be satisfactory, the effectiveness of the cooling or heating appliances of not less than l% of the number of units may be determined at a testing station in conformity with the provisions of sections 3.1, 3.2 and 3.3 of this appendix. If the results of the examinations and of the determination of effectiveness are acceptable, all the equipment in question may be kept in service in its initial class for a further period of six years.

7.	Test Reports

A test report of the type appropriate to the equipment tested shall be drawn up for each test in conformity with one or other of the models 1 to 10 hereunder.

MODEL No. 1 A

Test Report

Prepared in conformity with the provisions of the Agreement on the International Carriage of Perishable Foodstuffs and on the Special Equipment to be Used for such Carriage (ATP)

Test report No………..

Section 1

Specifications of the equipment (equipment other than tanks for the carriage of liquid foodstuffs)

Approved testing station/expert: l/

Name ………………………………………………………………………………………………

Address …………………………………………………………………………………………….

Type of equipment: 2/

Make…………………….Registration number…………………….Serial number……………….

Date of first entry into service …………………………………………………………………….

Tare 3/………………………………………..kg      Carrying capacity 3/ ………………………kg

Body:

Make and type ………………………………	 Identification number ………………………

Built by …………………………………………………………………………………………..

Owned or operated by ……………………………………………………………………………..

Submitted by……………………………………………………………………………………….

Date of construction ……………………………………………………………………………….

Principal dimensions:

Outside: length………….	 m, width ……………	m, height………………………… m

Inside:  length ……………	 m, width …………	m, height………………………… m

Total floor area of body………………………………………………………………………. m2

Usable internal volume of body ……………………………………………………………….. m3

MODEL No. 1 A (cont'd)

Total inside surface area Si of body …………………………………………………………… m2

Total outside surface area Se of body………………………………………………………….. m2

Mean surface area:S  =  Si.Se ………………………………………………………………. m2

Specifications of the body walls: 4/

Top ………………………………………………………………………………………………..

Bottom …………………………………………………………………………………………….

Sides 	………………………………………………………………………………………………

Structural peculiarities of body: 5/

Number,) of doors …………………………………………………………………….

positions) of vents ……………………………………………………………………

and dimensions ) of ice-loading apertures	……………………………………………………

Accessories 6/ 		……………………………………………………………………………….

………………………………………………………………………………..

K coefficient = …………………………………………………………………………………W/m2.K

1/	Delete as necessary (experts only in the case of tests carried out under ATP annex 1, appendix 2, sections 5 or 6).

2/	Wagon, lorry, trailer, semi-trailer, container, etc.

3/	State source of information.

4/	Nature and thickness of materials constituting the body walls, from the interior to the exterior, mode of construction, etc.

5/	If there are surface irregularities, show how Si and Se were determined.

6/	Meat bars, flettner fans, etc.

MODEL No. 1 B

Test Report

prepared in conformity with the provisions of the Agreement on the International Carriage of Perishable Foodstuffs and on the Special Equipment to be Used for such Carriage (ATP)

Test report No……………

Section 1

Specifications of tanks for the carriage of liquid foodstuffs

Approved testing station/expert: l/

Name ……………………………………………………………………………………………

Address …………………………………………………………………………………………….

Type of tank: 2/

Make ……………..	Registration number…………………	 Serial number ………….…….

Date of first entry into service 	…………………………………………………………………..

Tare 3/ …………………………………	 kg  Carrying capacity 3/ ……………………….. kg

Tank:

Make and type ………………………..	      Identification number ………………….………

Built by …………………………………………………………………………………………….

Owned or operated by ……………………………………………………………………………..

Submitted by ………………………………………………………………………………………

Date of construction ……………………………………………………………………………….

Principal dimensions:

Outside: length of cylinder ……….	 m, major axis ……….	 m, minor axis ……………… m

Inside:  length of cylinder ………..	 m, major axis ……….	 m, minor axis ……………… m

Usable internal volume ……………………………………………………………………… m3

MODEL No. 1 B (cont'd)

Internal volume of each compartment ………………………………………………………… m3

Total inside surface area Si of tank ……………………………………………………………..m2

Inside surface area of each compartment Si1 ………………., Si2 ………., …………………..m2

Total outside surface area Se of tank ………………………………………………………….. m2

Mean surface area of tank:S  =  Si.Se …………………………………………………….. m2

Specifications of the tank walls: 4/ 	…………………………………………………………………

Structural peculiarities of the tank: 5/ 	………………………………………………………………….

Number, dimensions and description of manholes ……………………………………………..

……………………………………………………………………………………………………

Description of manhole covers……..……………………………………………………………

…………………………………………………………………………………………………….

Number, dimensions and description of discharge piping……………………………………….

…………………………………………………………………………………..……………..

Accessories…….……………………………………………………………………………………..

……………………………………………………………………………………………………

1/	Delete as necessary (experts only in the case of tests carried out under ATP annex 1, appendix 2, sections 5 or 6).

2/	Wagon, lorry, trailer, semi-trailer, container, etc.

3/	State source of information.

4/	Nature and thickness of materials constituting the tank walls, from the interior to the exterior, mode of construction, etc.

5/	If there are surface irregularities, show how Si and Se were determined.

MODEL No. 2 A

Section 2

Measurement in accordance with ATP, annex 1, appendix 2, sub-section 2.1, of the overall coefficient of heat transfer of equipment other than tanks for liquid foodstuffs

Testing method: inside cooling/inside heating 1/

Date and time of closure of equipment's doors and other openings: ………………………………….….

Averages obtained for ……………	 hours of continuous operation

(from 		……………. a.m./p.m. to ………	 a.m./p.m.):

(a)	Mean outside temperature of body: 	Te = . . . . . . . . . . .  °C ± ……………………….…K

(b)	Mean inside temperature of body: 	Ti =  . . . . . . . . . . . . °C ± ………………………...K

(c)	Mean temperature difference achieved: ΔT = …………………………………………....K

Maximum temperature spread:

Outside body …………………………………………………………………………………….K

Inside body 	……………………………………………………………………………………...K

Mean temperature of walls of bodyTe +Ti2  ……………………………………………………...°C

Operating temperature of heat exchanger 2/ 	  ………………………………………………………..°C

Dew point of atmosphere outside body during continuous operation 2/

………………………………………………. °C ± ……………………………………………………K

Total duration of test …………………………………………………………………………………….h

Duration of continuous operation………………………………………………………………………..h

Power consumed in exchangers: W1 …………………………………………………………………W

Power absorbed by fans: W2 ………………………………………………………………………….W

Overall coefficient of heat transfer calculated by the formula:

Inside-cooling test 1/  	K  =  W1  −W2S .ΔT

Inside-heating test 1/  	K  =  W1 + W2S .ΔT

K =……………………….	W/m2.K

MODEL No. 2 A (cont'd)

Maximum error of measurement with test used ……………………………………………………….%

Remarks: 3/ 	 ………………………………………………………………………………………………

…………………………………………………………………………………………………………….

(To be completed only if the equipment does not have thermal appliances:)

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark IN/IR 1/.

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a) only for a period of not more than six years, that is until ……………………………………………………………………………………………………………

Done at:	…………………………………..

on		…………………………………..	…………………………………..

Testing Officer

l/	Delete as necessary.

2/	For inside-cooling test only.

3/	If the body is not parallelepipedic, specify the points at which the outside and inside temperatures were measured.

MODEL No. 2 B

Section 2

Measurement, in accordance with ATP annex 1, appendix 2, sub-section 2.2, of the overall coefficient of heat transfer of tanks for liquid foodstuffs

Testing method: inside heating

Date and time of closure of equipment's openings………………………………………………………..

Mean values obtained for ……………………………………………...	 hours of continuous operation

(from 		…………a.m./p.m. to …………….	a.m./p.m.):

(a)	Mean outside temperature of tank: Te = ……………	C ± ………………………….K

(b)	Mean inside temperature of tank:

Ti=Sin.TinSin				= …………..	°C± …………………..K

(c)	Mean temperature difference achieved: ΔT  ……………………………………………..K

Maximum temperature spread:

Inside tank ………………………………………………………………………………………K

Inside each compartment ………………………………………………………………………..K

Outside tank ……………………………………………………………………………………..K

Mean temperature of tank walls ………………………………………………………………………°C

Total duration of test ……………………………………………………………………………………h

Duration of continuous operation ………………………………………………………………………h

Power consumed in exchangers: W1 …………………………………………………………………W

Power absorbed by fans: W2 …………………………………………………………………………W

Overall coefficient of heat transfer calculated by the formula:

K  =  W1 + W2S .ΔT

K = ………….	 W/m2.K

MODEL No. 2 B (cont'd)

Maximum error of measurement with test used ………………………………………………………..%

Remarks: 1/ ……………………………………………………………………………………………....

…………………………………………………………………………………………………………….

(To be completed only if the equipment does not have thermal appliances:)

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark IN/IR. 2/

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a) only for a period of not more than six years, that is until ……………………………………………………………………………………………………………

Done at:………………………………..	………………………………….

on:	………………………………………	Testing Officer

l/	If the tank is not parallelepipedic, specify the points at which the outside and inside temperatures were measured.

2/	Delete as necessary.

MODEL No. 3

Section 2

Expert field check of the insulating capacity of equipment in service in accordance with ATP annex 1, appendix 2, section 5

The check was based on test report No……………………	dated ……………………………….…

issued by approved testing station expert (name and address)	………………………………………..

…………………………………………………………………………………………………………….

Condition when checked:

Top……………………………………………………………………………………………………

Side walls ………………………………………………………………………………………………

End wall………………………………………………………………………………………………

Bottom …………………………………………………………………………………………………

Doors and openings ……………………………………………………………………………………

Seals 	…………………………………………………………………………………………………

Cleaning drainholes ……………………………………………………………………………………

Air tightness	 	……………………………………………………………………………………

………………………………………………………………………………………………………..

K coefficient of the equipment when new (as shown in the previous test report) ……………………

………………………………………………………………………………………………… W/m2.K

Remarks: ………………………………………………………………………………………………

………………………………………………………………………………………………………..

According to the above test results the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for not more than three years, with the distinguishing mark IN/IR. 1/

Done at	………………………………………..

on:	………………………………………..	……………………………..

Testing Officer

1/	Delete as necessary.

MODEL No. 4 A

Section 3

Determination of the efficiency of cooling appliances of refrigerated equipment using ice or dry ice by an approved testing station in accordance with ATP annex 1, appendix 2, sub-section 3.1,

except 3.1.3 (b) and 3.1.3 (c)

Cooling appliance:

Description of cooling appliance …………………………………………………………………..

Nature of refrigerant ………………………………………………………………………………

Nominal refrigerant filling capacity specified

by manufacturer ……………………………………………………………………………….kg

Actual filling of refrigerant used for test ………………………………………………………kg

Drive independent/dependent/mains-operated 1/ …………………………………………………..

Cooling appliance removable/not removable 1/ ……………………………………………………

Manufacturer ………………………………………………………………………………………

Type, serial number ………………………………………………………………………………..

Year of manufacture ……………………………………………………………………………..

Filling device (description, where situated;

attach drawing if necessary) ………………………………………………………………………

……………………………………………………………………………………………………...

Inside ventilation appliances:

Description (number of appliances, etc.) …………………………………………………………..

Power of electric fans …………………………………………………………………………..W

Delivery rate ………………………………………………………………….……..……m3/h

Dimensions of ducts:  cross-section …………	m2, length …………………………….m

Air intake screen; description 1/ ……………………………………………………………………

1/	Delete if not applicable.

MODEL No. 4 A (cont'd)

Automatic devices 	………………………………………………………………………………………..

Mean temperatures at beginning of test:

Inside ………………………………...		°C ± …………………………………………….K

Outside ……………………………….	°C ± …………………………………………….K

Dew point in test chamber ……………	°C ± ………………………………………………K

Power of internal heating system ………………………………………………………………………W

Date and time of closure of equipment's doors and other openings ……………………………..…..

Record of mean inside and outside temperatures of body and/or curve showing variation

of these temperatures with time

……………………………………………………………………………………………………..

Remarks: …………………………………………………………………………………………………

……………………………………………………………………………………………………………..

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ……………………………………………………………………………………

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a) only for a period of not more than six years, that is until ………………….

Done at:	……………………………………….

on:	……………………………………….	………………………………..

Testing Officer

MODEL No. 4 B

Section 3

Determination of the efficiency of cooling appliances of refrigerated equipment with eutectic plates

by an approved testing station in accordance with ATP annex 1, appendix 2, sub-section 3.1,

except 3.1.3 (a) and 3.1.3 (c)

Cooling appliance:

Description 	………………………………………………………………………………………..

Nature of eutectic solution …………………………………………………………………………

Nominal eutectic solution filling capacity specified

by manufacturer ………………………………………………………………………………. kg

Latent heat at freezing temperature stated by manufacturer …………kJ/kg  at ………………°C

Cooling appliance removable/not removable 1/

Drive independent/dependent/mains-operated 1/

Manufacturer …………………………………………………………………………………….

Type, serial number ……………………………………………………………………………….

Year of manufacture ………………………………………………………………………………

Eutectic plates:  Make ………………………..	 Type ……………………………………….

Dimensions and number of plates, where situated;

distance from walls (attach drawing) ………………………………………………………………

…………………………………………………………………………………………………….

Total cold reserve stated by manufacturer for freezing

temperature of ……………………..	kJ  to 	…………………………………………………°C

Inside ventilation appliances (if any):

Description 	 ……………………………………………………………………………………..

Automatic devices 	……………………………………………………………………….………..

l/	Delete if not applicable.

MODEL No. 4 B (cont'd)

Mechanical refrigerator (if any):

Make 	…………………………………	Type 	………………….	 No. …………………

Where situated ……………………………………………………………………………………

Compressor:  Make …………………..	Type 	……………………………………………….

Type of drive …………………………………………………………………………………….

Nature of refrigerant ……………………………………………………………………………

Condenser ………………………………………………………………………………………….

Refrigerating capacity stated by the manufacturer for the specified freezing temperature and an outside temperature of + 30 °C	……………………….………………………………………W

Automatic devices:

Make	 ………………………………	Type ………………………………………….……….

Defrosting (if any) ……………………………………………………………………………….

Thermostat ……………………………………………………………………………………….

LP pressostat ………………………………………………………………………………………

HP pressostat ………………………………………………………………………………………

Relief valve ………………………………………………………………………………………..

Others	……………………………………………………………………………………….

Accessory devices:

Electrical heating devices of the door joint:

Capacity by linear metre of the resistor …………………………………………………….W/m

Linear length of the resistor ……………………………………………………………………m

Mean temperatures at beginning of test:

Inside ……………………………	°C ± …………………………………………………..K

Outside ……………………………	°C ± …………………………………………………….K

Dew point in test chamber …………	°C ± ……………………………………………………K

MODEL No. 4 B (cont'd)

Power of internal heating system ……………………………………………………………………..W

Date and time of closure of equipment's

doors and openings ……………………………………………………………………………………..

Period of accumulation of cold …………………………………………………………………………h

Record of mean inside and outside temperatures of body

and/or curve showing variation of these temperatures

with time ………………………………………………………………………………………………..

………………………………………………………………………………………………………….

Remarks: …………………………………………………………………………………………………..

……………………………………………………………………………………………………………

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ……………………………………………………………………………………….

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a) only for a period of not more than six years, that is until …………………..

Done at:	……………………………………………...

on:	……………………………………………...	……………………………….

Testing Officer

MODEL No. 4 C

Section 3

Determination of the efficiency of cooling appliances of refrigerated equipment using liquefied gases by an approved testing station in accordance with ATP annex l, appendix 2, sub-section 3.1,

except 3.1.3 (a) and 3.1.3 (b)

Cooling appliance:

Description

…………………………………………………………………………………………………...

Drive independent/dependent/mains-operated 1/

Cooling appliance removable/not removable 1/

Manufacturer ……………………………………………………………………………………

Type, serial number …………………………………………………………………………….

Year of manufacture ……………………………………………………………………………

Nature of refrigerant ……………………………………………………………………………

Nominal refrigerant filling capacity specified

by manufacturer ………………………………………………………………………………kg

Actual filling of refrigerant used for test ………………………………………………………..kg

Description of tank	 ………………………………………………………………………………

Filling device (description, where situated) ………………………………………………………

Inside ventilation appliances:

Description (number, etc.) ………………………………………………………….	……….

Power of electric fans …………………………………………………………………………………..W

Delivery rate …………………………………………………………………………………m3/h

Dimensions of ducts:  cross-section ………...…….	m2, length …………………………………m

Automatic devices 	………………………………………………………………………………………..

l/	Delete if not applicable.

MODEL No. 4 C (cont'd)

Mean temperatures at beginning of test:

Inside	 ………………………..……….	°C ± ………………………………………………K

Outside ……………………………….	°C ± ………………………………………………K

Dew point in test chamber ……………	°C ± ………………………………………………K

Power of internal heating system ………………………………………………………………………W

Date and time of closure of equipment's

doors and openings ……………………………………………………………………………………….

Record of mean inside and outside temperatures of body and/or curve showing

variation of these temperatures with time ………………………………………………………………..

…………………………………………………………………………………………………………….

Remarks:…………………………………………………………………………………………………

……………………………………………………………………………………………….…………….

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ……………………………………………………………………………………….

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a), only for a period of not more than six years, that is until ………………….

Done at:	…………………………………………….

on:	…………………………………………….	…………………………………

Testing Officer

MODEL No. 5

Section 3

Determination of the efficiency of cooling appliances of mechanically refrigerated equipment

by an approved testing station in accordance with ATP annex 1,

appendix 2, sub-section 3.2

Mechanical refrigerating appliances:

Drive independent/dependent/mains-operated 1/

Mechanical refrigerating appliances removable/not removable 1/

Manufacturer …………………………………………………………………………………….

Type, serial number ………………………………………………………………………………..

Year of manufacture ……………………………………………………………………………….

Nature of refrigerant and filling capacity ………………………………………………………..

Effective refrigerating capacity stated by manufacturer for an outside temperature of + 30 °C

and an inside temperature of:

0 °C	………………………………………………………………………………….. W

-10 °C	…………………………………………………………………………….W

-20 °C	………………………………………………………………………………W

Compressor:

Make	 …………………………………	Type ……………………………………………….

Drive: electric/thermal/hydraulic 1/

Description ………………………………………………………………………………………….

Make ………………	Type …………..	power …………..	kW …	at …………….rpm

Condenser and evaporator ………………………………………………………………………

Motor element of fan(s):  make ……………	type ……………..	number ………………………

power	 …………………………………	kW	at………………………………………rpm

1/	Delete if not applicable.

MODEL No. 5 (cont'd)

Inside ventilation appliances:

Description (number of appliances, etc.) ………………………………………………………….

Power of electric fans ………………………………………………………………………W

Delivery rate ………………………………………………………………………………….m3/h

Dimensions of ducts:  cross-section ……………	m2, length …………………………………m

Automatic devices:

Make ………………………………………	   Type …………………………………………

Defrosting (if any) ……………………………………………………………………………….

Thermostat ………………………………………………………………………………………

LP pressostat …………………………………………………………………………………….

HP pressostat ……………………………………………………………………………………

Relief valve ………………………………………………………………………………………

Others	………………………………………………………………………………………

Mean temperatures at beginning of test:

Inside temperature …………………		°C ± ……………………………………………K

Outside temperature ……………….		°C ± …………………………………………….K

Dew point in test chamber ………….		°C ± ………………………………………….…K

Power of internal heating system ……………………………………………………………………..W

Date and time of closure of equipment's

doors and other openings …………………………………………………………………………………

Record of mean inside and outside temperatures of body and/or curve showing variation

of these temperatures with time …………………………………………………………………………..

…………………………………………………………………………………………………………

MODEL No. 5 (cont'd)

Time between beginning of test and attainment

of prescribed mean inside temperature of body ……………………………………………………….h

Remarks: ………………………………………………………………………………………………..

……………………………………………………………………………………………………………..

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ………………………………………………………………………………………

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a), only for a period of not more than six years, that is until ……………………..

Done at:	……………………………….

on:	……………………………….	……………………………………

Testing Officer

MODEL No. 6

Section 3

Determination of the efficiency of heating appliances of heated equipment by an approved testing station in accordance with ATP annex 1, appendix 2, sub-section 3.3

Heating appliance:

Description …………………………………………………………………………………………..

Drive independent/dependent/mains-operated 1/

Heating appliance removable/not removable 1/

Manufacturer …………………………………………………………………………………………

Type, serial number ……………………………………………………………………………….

Year of manufacture ……………………………………………………………………………….

Where situated ……………………………………………………………………………………..

Overall area of heat exchange surfaces ………………………………………………………..m2

Effective power rating as specified by manufacturer ………………………………………..kW

Inside ventilation appliances:

Description (number of appliances, etc.) ………………………………………………………...

Power of electric fans ………………………………………………………………………….W

Delivery rate ………………………………………………………………………………….m3/h

Dimensions of ducts:  cross-section ……………….	 m2, length …………………………m

Mean temperatures at beginning of test:

Inside temperature 	………………………………	°C ± ………………………………...K

Outside temperature …………………………….	°C ± …………………………………K

Date and time of closure of equipment's

doors and other openings ………………………………………………………………………………

1/	Delete if not applicable.

MODEL No. 6 (cont'd)

Record of mean inside and outside temperatures of body and/or

curve showing variation of these temperatures with time ………………………………………………..

………………………………………………………………………………………………….………….

Time between beginning of test and attainment of prescribed

mean inside temperature of body ………………………………………………………………………..h

Where applicable, mean heating output during test to

maintain prescribed temperature difference 2/ between

inside and outside of body ……………………………………………………………………………..W

Remarks: ………………………………………………………………………………………………….

…………………………………………………………………………………………………………….

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ……………………………………………………………………………………

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a), only for a period of not more than six years, that is until ………………

Done at:	………………………………………….

on:	………………………………………….	………………………………..

Testing Officer

2/	Increased by 35% for new equipment.

MODEL No. 7

Section 3

Expert field check of the efficiency of cooling appliances of refrigerated equipment in service in accordance with ATP annex 1, appendix 2, sub-section 6.1

The check was conducted on the basis of report No………………………………………………………

dated …………………………………………………………………………….,  issued by approved testing station/expert (name, address) …………………………………………………………………….

…………………………………………………………………………………………………………….

Cooling appliance:

Description ………………………………………………………………………………………

Manufacturer …………………………………………………………………………………….

Type, serial number ………………………………………………………………………….….

Year of manufacture …………………………………………………………………………….

Nature of refrigerant ………………………………………………………………………………

Nominal refrigerant filling capacity

specified by manufacturer ……………………………………………………………………...kg

Actual filling of refrigerant used for test ………………………………………………………..kg

Filling device (description, where situated) ……………………………………………………….

Inside ventilation appliances:

Description (number of appliances, etc.) …………………………………………………………

Power of electric fans ………………………………………………………………………….W

Delivery rate ………………………………………………………………………………..m3/h

Dimensions of ducts:  cross-section ……………	 m2, length ………………………………..m

Condition of cooling appliance and ventilation appliances ………………………………………

……………………………………………………………………………………………………

……………………………………………………………………………………………………

Inside temperature attained …………………………………………………………………...°C

At an outside temperature of ……………………………………………………………………°C

MODEL No. 7 (cont'd)

Inside temperature of the equipment before the refrigerating appliance is started …………………….°C

Total running time of the refrigerating unit ……………………………………………………………..h

Time between beginning of test and attainment of prescribed

mean inside temperature of body ………………………………………………………………………. h

Check on operation of thermostat ……………………………………………………………………….

For refrigerated equipment with eutectic plates:

Period of operation of the cooling appliance for freezing

of the eutectic solution ………………………………………………………………………………….h

Period during which inside air temperature is maintained

after the appliance is switched off ……………………………………………………………………..h

Remarks: …………………………………………………………………………………………….

…………………………………………………………………………………………………………….

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than three years, with the distinguishing mark ……………………………………………………………………………………

Done at:	……………………………………………

on:	……………………………………………	……………………………..

Testing Officer

MODEL No. 8

Section 3

Expert field check of the efficiency of cooling appliances of mechanically refrigerated equipment in service in accordance with ATP annex 1, appendix 2, sub-section 6.2

The check was conducted on the basis of report No………………	 dated ………………………….

issued by approved testing station/expert (name, address) ……………………………………………….

…………………………………………………………………………………………………………….

Mechanical refrigerating appliances:

Manufacturer ………………………………………………………………………………………

Type, serial number ………………………………………………………………………………..

Year of manufacture ……………………………………………………………………………….

Description ………………………………………………………………………………………

Effective refrigerating capacity specified by manufacturer for an outside temperature of +30 °C  and an inside temperature of

0 °C 	………………………………………………………………………………W

- 10 °C 	…………………………………………………………………………….W

- 20 °C 	………………………………………………………………………………W

Nature of refrigerant and filling capacity …………………………………………………………….kg

Inside ventilation appliances:

Description (number of appliances, etc.) ………………………………………………………….

Power of electric fans …………………………………………………………………………W

Delivery rate ……………………………………………………………………	……..m3/h

Dimensions of ducts: cross-section  ………………	 m2, length ………………………………..m

Condition of mechanical refrigerating appliance and inside ventilation appliances …………….

……………………………………………………………………………………………………..

MODEL No. 8 (cont'd)

Inside temperature attained …………………………………………………………………………….°C

At an outside temperature of …………………………………………………………………..°C

and with a relative running time of ……………………………………………………………%

Running time …………………………………………………………………………………… h

Check on operation of thermostat ………………………………………………………………………

Remarks: ……………………………………………………………………………………………….

……………………………………………………………………………………………………………..

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3 valid for a period of not more than three years, with the distinguishing mark ………………………………………………………………………………………

Done at:	……………………………………….

on:	…………………………………..……	…………………………….

Testing Officer

MODEL No. 9

Section 3

Expert field check of the efficiency of heating appliances of heated equipment in service in accordance with ATP annex 1, appendix 2, sub-section 6.3

The check was conducted on the basis of report No. ………………..	 dated ………………………….

issued by approved testing station/expert (name, address) ……………………………………………..

…………………………………………………………………………………………………………..

Mode of heating:

Description ………………………………………………………………………………………

Manufacturer …………………………………………………………………………………….

Type, serial number ………………………………………………………………………………

Year of manufacture …………………………………………………………………………..

Where situated …………………………………………………………………………………….

Overall area of heat exchange surfaces	 ……………………………………………………….m2

Effective power rating as specified by manufacturer ………………………………………….kW

Inside ventilation appliances:

Description (number of appliances, etc.) ……………………………………………………….

Power of electric fans ………………………………………………………………………….W

Delivery rate ………………………………………………………………………………..m3/h

Dimensions of ducts: cross-section ……………………	 m2, length …………………………… m

Condition of heating appliance and inside ventilation appliances ……………………………………….

……………………………………………………………………………………………………………..

…………………………………………………………………………………………………………….

Inside temperature attained …………………………………………………………………………..°C

MODEL No. 9 (cont'd)

At an outside temperature of ………………………………………………………………….°C

and with a relative running time of …………………………………………………….………..%

Running time ……………………………………………………………………………………..h

Check on operation of thermostat ………………………………………………………………………..

Remarks: ………………………………………………………………………………………………….

…………………………………………………………………………………………………………….

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than three years, with the distinguishing mark ………………………………………………………………………………………

Done at:	……………………………………

on:	……………………………………	………………………………..

Testing Officer

MODEL No. 10

TEST REPORT

prepared in conformity with the provisions of the Agreement on the International Carriage of Perishable Foodstuffs and on the Special Equipment to be Used for such Carriage (ATP)

Test Report No……………

Determination of the effective refrigerating capacity of a refrigeration unit

in accordance with section 4 of ATP annex 1, appendix 2

Approved testing station

Name: ………………………………………………………………………………………………….….

Address: …………………………………………………………………………………………………..

Refrigeration unit presented by: ……………………………………………………………………...

………………………………………………………………………………………………………...

…………………………………………………………………………………………………………

(a)	Technical specifications of the unit

Date of manufacture: ……………………………………	 Make:  …………………………………….

Type:  ………………………………………………	 Serial No: …………………………………..

Category 1/

Self-contained/not self-contained

Removable/not removable

Single unit/assembled components

Description:………………………………………………………………………………………………

……………………………………………………………………………………………………………..

……………………………………………………………………………………………………………

Compressor:		Make: …………………………….		Type: …………………………………

Number of cylinders: …………….		Cubic capacity: …………………….

Nominal speed of rotation: ……………………………………………….……. rpm

Methods of drive 1/:  electric motor, separate internal combustion engine,

vehicle engine, vehicle motion

Compressor drive motor:  (See footnotes 1 and 2)

Electrical:		Make: ………………………		Type: …………………………………….

Power: ……………………….	kW 	at ……………………………………rpm

Supply voltage ………………….	 V	Supply frequency ………………..Hz

MODEL No. 10 (cont’d)

Internal combustion engine:	Make: ………………………..		Type: …………………………

Number of cylinders: …………		Cubic capacity: ………………..

Power:………………………	kW 	 at ………………………….rpm					Fuel: ………………………..

Hydraulic motor:			Make:………………………….		 Type: ………………………….

Method of drive: ………………

Alternator:				Make: …………………………		  Type: ………………………..

Speed of rotation: .			(nominal speed given by the manufacturer:

(

(…………………………………………………………………….rpm

(

(minimum speed:  ………………………………………………….rpm

Refrigerant fluid:	………………………………………………………………………………………..

| Heat exchangers |  | Condenser | Evaporator |
| --- | --- | --- | --- |
| Make-type |  |  |  |
| Number of tubes |  |  |  |
| Fan pitch (mm)2/ |  |  |  |
| Tube: nature and diameter (mm)2/ |  |  |  |
| Exchange surface area (m2)2/ |  |  |  |
| Frontal area (m2) |  |  |  |
| FANS | Number |  |  |
|  | Number of blades per fan |  |  |
|  | Diameter (mm) |  |  |
|  | Nominal power (W)2/3/ |  |  |
|  | Total nominal output at a pressure of . . . . . . Pa (m3/h)2/ |  |  |
|  | Method of drive |  |  |

Expansion valve:	Make: …………………………..	 Model: ……………………………………

Adjustable: 1/ …………………..	 Not adjustable: 1/	…………………………..

Defrosting device: ……………………………………………………………………………………….

Automatic device:  …………………………………………………………………………………….

MODEL No.10 (cont’d)

Results of measurements and refrigerating performance

(Mean temperature of the air to the inlet(s) of the refrigeration unit . . . . . °C)

TRANS/WP.11/2005/10

page 67

| Speed of Rotation |  |  |  | Power of internal fan heater | Power absorbed by the unit cooler fan 4/ | Fuel or electrical power consumption | Mean temperature around the body | Internal temperature |  | Effective refrigerating capacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fans 3/ | Alternator 3/ | Compressor 3/ |  |  |  |  | Mean | Inlet to evaporator |  |
|  | rpm | rpm | rpm | W | W | W or l/hr | °C | °C | °C | W |
| Nominal | ....................…..………...………...………….. | ....................…..………...………...…………. | .....................…………..………..………….. | ....................................................…..……… | ........................................................... | .........................................................………. | ....................................................................…... | ............................……..…………… | .........................……..…...………… | ......................................................................... |
| Minimal | .....................….………...………..………….. | ....................…….……..……..….………….. | .....................….………...…….….…………... | ...............................................….....…….……. | ........................................................… | ...................................................................... | ...................................................................... | ..........................…..……....……..… | ...............…....………..…..………… | ........................................................................... |

MODEL No. 10 (cont’d)

(b)	Test method and results:

Test method 1/:  heat balance method/enthalpy difference method

In a calorimeter box of mean surface area = ………………………………………………….. m2

measured value of the U-coefficient of a box fitted with a refrigeration unit:……. W/°C,

at a mean wall temperature of …………………..°C.

In an item of transport equipment:

measured value of the U-coefficient of an item of transport equipment fitted with a refrigeration unit: …………………………………………………………………..W/°C, at a mean wall temperature of ………………………………………………………….°C.

Method employed for the correction of the U-coefficient of the body as a function of the mean wall temperature of the body: ………………………………………………………………………………….

…………………………………………………………………………………………………………….

………………………………………………………………………………………………………….

Maximum errors of determination of:

U-coefficient of the body ……………………………………………………………………….

refrigerating capacity of the unit ………………………………………………………………..

(c)	Checks

Temperature regulator:  Setting ………………..	 Differential ……………………………..°C

Functioning of the defrosting device 1/:  satisfactory/unsatisfactory

Air flow volume leaving the evaporator: 	value measured ………………………………..m3/h

at a pressure of …………………………………Pa

Existence of a means of supplying heat to the evaporator for setting the thermostat between 0 and 12 °C 1/:  	yes/no

(d)	Remarks

…………………………………………………………………………………………………….

………………………………………………………………………………………………………

……………………………………………………………………………………………………..

Done at:	……………………………………

On: 	……………………………………	…………………………

Testing Officer

1/	Delete where applicable.

2/	Value indicated by the manufacturer.

3/	Where applicable.

4/	Enthalpy difference method only.

Annex 1, Appendix 3

A.	FORM OF CERTIFICATE FOR INSULATED, REFRIGERATED, MECHANICALLY

REFRIGERATED OR HEATED EQUIPMENT USED FOR THE INTERNATIONAL

CARRIAGE OF PERISHABLE FOODSTUFFS BY LAND

1/

6/

|  |  | EQUIPMENT |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| INSULATED | REFRIGERATED | MECHANICALLY REFRIGERATED | HEATED |  | MULTI-TEMPERATURE7/ | 5/ |  |  |

CERTIFICATE 2/

issued pursuant to the Agreement on the International Carriage

of Perishable Foodstuffs and on the Special Equipment

to be Used for such Carriage (ATP)

l.	Issuing authority 	………………………………………………………………………………………..

2.	Equipment 3/ 	………………………………………………………………………………………..

3.	Identification number	…………………..	allotted by	……………………………………………….

4.	Owner or operated by	………………………………………………………………………………….

5.	Submitted by	………………………………………………………………………………………..

6.	Is approved as 4/ 	………………………………………………………………………………………..

6.l. 	with one or more thermal appliances which (is) (are):

6.l.l.	independent;		)

6.l.2.	not independent;		)

6.l.3.	removable;			) 5/

6.l.4.	not removable.		)

l/	Distinguishing sign of the country, as used in international road traffic.

2/	The blank certificate shall be printed in the language of the issuing country and in English, French or Russian; the various items shall be numbered as in the above model.

3/	State type (wagon, lorry, trailer, semi-trailer, container, etc.); in the case of tank equipment for the carriage of liquid foodstuffs, add the word "tank".

4/	Enter here one or more of the descriptions listed in appendix 4 of this annex, together with the corresponding distinguishing mark or marks.

5/	Strike out what does not apply.

6/	The number (figures, letters, etc.) indicating the authority issuing the certificate and the approval reference.

7/	The test procedure is not yet determined within the ATP Agreement.

Multi-temperature equipment is an insulated equipment with two or more compartments for different temperatures in each compartment.

7.		Basis of issue of certificate

7.l.		This certificate is issued on the basis of:

7.l.l.	tests of the equipment;					)

7.l.2.	conformity with a reference item of equipment;	)

7.l.3.	a periodic inspection;					)  l/

7.l.4.	transitional provisions.					)

7.2.	If the certificate is issued on the basis of a test or by reference to an item of equipment of the same type which has been tested, specify:

7.2.l.	the testing station …………………………………………………………………….

7.2.2.	the nature of the tests 2/ ……………………………………………………………

……………………………………………………………………………………..

7.2.3.	the number(s) of the report(s) ………………………………………………………..

7.2.4.	the K coefficient ……………………………………………………………………..

7.2.5.	the effective refrigerating capacity 3/ at an outside temperature of 30°C and an inside temperature

|  | Nominal capacity | Evaporator 14/ | Evaporator 24/ |  | Evaporator 34/ |
| --- | --- | --- | --- | --- | --- |
| of ...°C | ………… W | ………… W |  | ……………. W | ………… W |
| of ...°C | ………… W | ………… W |  | ……………. W | …………. W |
| of ...°C | ………… W | ………… W |  | ……………. W | …………. W |

8.		This certificate is valid until ……………………………………………………………………….

8.l.	provided that:

8.l.l.	the insulated body (and, where applicable, the thermal appliance) is maintained in good condition;

8.l.2.	no material alteration is made to the thermal appliances; and

8.l.3.	if the thermal appliance is replaced, it is replaced by an appliance of equal or greater refrigerating capacity.

9.		Done at: 							 10.	on:

(The competent authority)

l/	Strike out what does not apply.

2/	For example:  insulating capacity or efficiency of thermal appliances.

3/	Where measured in conformity with the provisions of appendix 2, paragraph 3.2.7, to this annex.

4/	The effective cooling capacity of each evaporator depends on the number of evaporators fixed at the condensing unit.

# Comment to Item 8.1.2:

The replacement of components of the thermal appliance does not constitute a material alteration, in as much as replacement components do not reduce the quality of the appliance performance.

B. 	Certification plate of compliance of the equipment, as provided for in annex 1, appendix 1, paragraph 3

1.		The certification plate shall be affixed to the equipment permanently and in a clearly visible place adjacent to any other approval plate issued for official purposes.  The plate, conforming to the model reproduced below, shall take the form of a rectangular, corrosion-resistant and fire-resistant plate measuring at least 160 mm by 100 mm.  The following particulars shall be indicated legibly and indelibly on the plate in at least the English or French or Russian language:

(a)	the Latin letters "ATP" followed by the words "APPROVED FOR TRANSPORT OF PERISHABLE FOODSTUFFS";

(b)	"APPROVAL NUMBER" followed by the distinguishing sign (in international road traffic) of the State in which the approval was granted and the number (figures, letters, etc.) of the approval reference;

(c)	"EQUIPMENT NUMBER" followed by the individual number assigned to identify the particular item of equipment (which may be the manufacturer's number);

(d)	"ATP MARK" followed by the distinguishing mark prescribed in annex l, appendix 4, corresponding to the class and the category of the equipment;

(e)	"VALID UNTIL" followed by the date (month and year) when the approval of the unit of equipment expires.  If the approval is renewed following a test or inspection, the subsequent date of expiry may be added on the same line.

2.		The letters "ATP" and the letters of the distinguishing mark should be approximately 20 mm high.  Other letters and figures should not be less than 5 mm high.

Annex l, Appendix 4

DISTINGUISHING MARKS TO BE AFFIXED TO SPECIAL EQUIPMENT

The distinguishing marks prescribed in appendix 1, paragraph 4 to this annex shall consist of capital Latin letters in dark blue on a white ground. The height of the letters shall be at least 100 mm for the classification marks and at least 50 mm for the expiry dates. For special equipment, such as a laden vehicle with maximum mass not exceeding 3.5 t, the height of the classification marks could likewise be 50 mm and at least 25 mm for the expiry dates.

The classification and expiry marks shall at least be affixed externally on both sides in the upper corners near the front.

The marks shall be as follows:

Equipment	Distinguishing

mark

Normally insulated equipment	IN

Heavily insulated equipment	IR

Class A refrigerated equipment with normal insulation	RNA

Class A refrigerated equipment with heavy insulation	RRA

Class B refrigerated equipment with heavy insulation	RRB

Class C refrigerated equipment with heavy insulation	RRC

Class D refrigerated equipment with normal insulation	RND

Class D refrigerated equipment with heavy insulation	RRD

Class A mechanically refrigerated equipment with normal

insulation	FNA

Class A mechanically refrigerated equipment with heavy

insulation	FRA

Class B mechanically refrigerated equipment with heavy

insulation	FRB

Class C mechanically refrigerated equipment with heavy

insulation	FRC

Class D mechanically refrigerated equipment with normal

insulation	FND

Class D mechanically refrigerated equipment with heavy

insulation	FRD

Equipment	Distinguishing

mark

Class E mechanically refrigerated equipment with heavy

insulation	FRE

Class F mechanically refrigerated equipment with heavy

insulation	FRF

Class A heated equipment with normal insulation	CNA

Class A heated equipment with heavy insulation	CRA

Class B heated equipment with heavy insulation	CRB

If the equipment is fitted with a removable or non-independent thermal appliance and if special conditions exist for the use of the thermal appliance, the distinguishing mark or marks shall be supplemented by the letter X in the following cases:

1.	FOR REFRIGERATED EQUIPMENT:

Where the eutectic plates have to be placed in another chamber for freezing;

2.	FOR MECHANICALLY REFRIGERATED EQUIPMENT:

2.1	Where the compressor is powered by the vehicle engine;

2.2	Where the refrigeration unit itself or a part is removable, which would prevent its functioning.

The date (month, year) entered under section A, item 8 in appendix 3 of this annex as the date of expiry of the certificate issued in respect of the equipment shall be quoted under the distinguishing mark or marks aforesaid.

Model:

02   =	month (February)	) of expiry of the

FRC

02 - 201l

2011=	year			) certificate

Annex 2

###### SELECTION OF EQUIPMENT AND TEMPERATURE CONDITIONS

TO BE OBSERVED FOR THE CARRIAGE OF QUICK

(DEEP)-FROZEN AND FROZEN FOODSTUFFS

1.	For the carriage of the following quick (deep)-frozen and frozen foodstuffs, the transport equipment has to be selected and used in such a way that during carriage the highest temperature of the foodstuffs at any point of the load does not exceed the indicated temperature.

By that means the equipment used for the transport of quick-frozen foodstuffs other than railway equipment shall be fitted with the device referred to in appendix 1 to this annex. If however one should proceed to the verification of the temperature of the foodstuff, this shall be done according to the procedure laid down in appendix 2 to this annex.

2.	Accordingly, the temperature of the foodstuffs at any point in the load must be at or below the indicated value on loading, during carriage and on unloading.

3.	Where it is necessary to open the equipment, e.g. to carry out inspections, it is essential to ensure that the foodstuffs are not exposed to procedures or conditions contrary to the objectives of this annex and those of the International Convention on the Harmonization of Frontier Controls of Goods.

4.	During certain operations, such as defrosting the evaporator of mechanically refrigerated equipment, a brief rise of the temperature of the surface of the foodstuffs of not more than 3 °C in a part of the load, e.g. near the evaporator, above the appropriate temperature may be permitted.

Ice cream	………………………………………………………………………….	-20 °C

Frozen or quick (deep)-frozen fish, fish products,

molluscs and crustaceans and all other

quick (deep)-frozen foodstuffs 	……………………………………………….	-18 °C

All frozen foodstuffs (except butter)	………………………………………..	-12 °C

Butter 	……………………………………………………………………	-10 °C

Deep-frozen and frozen foodstuffs mentioned below to be

immediately further processed at destination: 1/

Butter

Concentrated fruit juice

Annex 2, Appendix 1

MONITORING OF AIR TEMPERATURES FOR TRANSPORT OF

PERISHABLE FOODSTUFFS QUICK-FROZEN

The transport equipment must be fitted with a suitable recording instrument to monitor, at frequent and regular intervals, the air temperatures to which quick-frozen foodstuffs intended for human consumption are subjected.

The measuring instruments must be approved by the competent authorities of the country in which the means of transport is registered.

Temperature recordings obtained in this manner must be dated and stored by the operator for at least one year or longer, according to the nature of the food.

However, for transport equipment in service at the date of the entry into force of this appendix, 1/ the above provisions will be progressively applicable within three years after that date.

Comments to Annex 2, Appendix 1:

1.	The reason for monitoring is to enable the operator to know that the refrigeration and air distribution system are functioning correctly, and to act as the first step in an enforcement of inspection process.  Thus, temperature monitoring and presentation of the data produced by such devices, would facilitate inspection taking place at the end of, or even during a journey. It enhances control of temperature and could be used as part of any defence during trade or legal disputes which might arise.

2.	The recording of the data may be mechanical (chart recorder) or electronic, providing a continuously recorded trace or an intermittent record from time of loading to that of unloading.  The interval between each temperature measurement depends on the length of the journey.  Thus for journeys of more than 8 hours to less than 5 days, a maximum interval of 1 hour could be used.  Clear identification of separate loads and deliveries should also be indicated on the record.

_________________

1/	The date of entry into force of this appendix is 13 February 1996.

Annex 2, Appendix 2

PROCEDURE FOR THE SAMPLING AND MEASUREMENT OF TEMPERATURE

FOR CARRIAGE OF CHILLED, FROZEN AND QUICK-FROZEN

PERISHABLE FOODSTUFFS

## A.	GENERAL CONSIDERATIONS

1.	Inspection and measurement of temperatures stipulated in annexes 2 and 3 should be carried out so that the foodstuffs are not exposed to conditions detrimental to the safety or quality of the foodstuffs.  Measuring of food temperatures should be carried out in a refrigerated environment, and with the minimum delays and minimum disruption of transport operations.

2.	Inspection and measurement procedures, as referred to in paragraph 1, shall preferably be carried out at the point of loading or unloading.  These procedures should not normally be carried out during transport, unless serious doubt exists about the conformity of the temperatures of the foodstuffs stipulated in annexes 2 and 3.

3.	Where possible, the inspection should take account of information provided by temperature monitoring devices during the journey before selecting those loads of perishable foodstuffs for sampling and measurement procedures.  Progression to temperature measurement of the food should only be undertaken where there is reasonable doubt of the temperature control during carriage.

4.	Where loads have been selected, a non-destructive measurement (between-case or between-pack) should at first be used.  Only where the results of the non-destructive measurement do not conform with the temperatures laid down in annexes 2 or 3 (taking into account allowable tolerances), are destructive measurements to be carried out.  Where consignments or cases have been opened for inspection, but no further action has been taken, they should be resealed giving the time, date, place of inspection, and the official stamp of the inspection authority.

## B.	SAMPLING

5.	The types of package selected for temperature measurement shall be such that their temperature is representative of the warmest point of the consignment.

6.	Where it is necessary to select samples during transport whilst the consignment is loaded, two samples should be taken from the top and bottom of the consignment adjacent to the opening edge of each door or pair of doors.

7.	Where samples are taken during unloading of the consignment, four samples should be chosen from any of the following locations:

-	top and bottom of the consignment adjacent to the opening edge of the doors;

-	top rear corners of the consignment (i.e. furthest away from the refrigeration unit);

-	centre of the consignment;

-	centre of the front surface of the consignment (i.e. closest to the refrigeration unit);

-	top or bottom corners of the front surface of the consignment (i.e. closest to the return air intake of the refrigeration unit).

8.	In the case of chilled foods in annex 3, samples should also be taken from the coldest location to ensure that freezing has not occurred during transportation.

C.	TEMPERATURE MEASUREMENT OF PERISHABLE FOODSTUFFS

9.	The temperature measuring probe should be precooled to as close to the product temperature as possible before measurement.

I.	Chilled foods

10.	Non-destructive measurement.  Measurement between-case or between-pack should be made with a probe with a flat head, which gives a good surface contact, low thermal mass, and high thermal conductivity.  When placing the probe between the cases or food packs, there should be sufficient pressure to give a good thermal contact, and sufficient length of probe inserted to minimize conductivity errors.

11.	Destructive measurement.  A probe with a rigid, robust stem and sharpened point should be used, made from a material which is easy to clean and disinfect.  The probe should be inserted into the centre of the food pack, and the temperature noted when a steady reading is reached.

II.	Frozen and quick-frozen foods

12.	Non-destructive measurement.  Same as paragraph 10.

13.	Destructive measurement.  Temperature probes are not designed to penetrate frozen foods.  Therefore it is necessary to make a hole in the product in which to insert the probe.  The hole is made by a precooled product penetration instrument, which is a sharp pointed metallic instrument such as an ice punch, hand drill or an auger.  The diameter of the hole should provide a close fit to that of the probe.  The depth to which the probe is inserted will depend on the type of product:

(i)	Where product dimensions allow, insert the probe to a depth of 2.5 cm from the surface of the product;

(ii)	Where (i) is not possible because of the size of the product, the probe should be inserted to a minimum depth from the surface of 3 to 4 times the diameter of the probe;

(iii)	It is not possible or practical to make a hole in certain foods because of their size or composition e.g. diced vegetables.  In these cases, the internal temperature of the food package should be determined by insertion of a suitable sharp-stemmed probe to the centre of the pack to measure the temperature in contact with the food.

After inserting the probe, the temperature should be read when it has reached a steady value.

## D.	GENERAL SPECIFICATIONS FOR THE MEASURING SYSTEM

14.	The measuring system (probe and read-out) used in determining temperature shall meet the following specifications:

(i)	the response time should achieve 90% of the difference between the initial and final reading within three minutes;

(ii)	1/ the system must have an accuracy of + 0.5 °C within the measurement range - 20 °C to + 30 °C;

(iii)	1/ the measuring accuracy must not change by more than 0.3 °C during operation in the ambient temperature range – 20  C to + 30 °C;

(iv)	the display resolution of the instrument should be 0.1 °C;

(v)	1/ the accuracy of the system should be checked at regular intervals;

(vi)	the system should have a current certificate of calibration from an approved institution;

(vii)	the electrical components of the system should be protected against undesirable effects due to condensation of moisture;

(viii)	the system should be robust and shock proof.

#### E.	ALLOWABLE TOLERANCES IN THE MEASUREMENT OF TEMPERATURE

15.	Certain tolerances should be allowed in the interpretation of temperature measurements:

(i)	operational - in the case of frozen and quick-frozen foods, a brief rise of up to 3 °C on the temperature permitted in annex 2 is allowed for the surface temperature of the food;

(ii)	methodology - non-destructive measurement can give up to a maximum of 2 °C difference in the reading compared to the true product temperature measurement, especially with the thickness of cardboard in case packaging.  This tolerance does not apply to the destructive measurement of temperature.

Annex 3

SELECTION OF EQUIPMENT AND TEMPERATURE CONDITIONS TO BE

OBSERVED FOR THE CARRIAGE OF CHILLED FOODSTUFFS

1.	For the carriage of the following chilled foodstuffs, the transport equipment has to be selected and used in such a way that during carriage the highest temperature of the foodstuffs at any point of the load does not exceed the indicated temperature.  If, however the verification of the temperature of the foodstuff is carried out, it shall be done according to the procedure laid down in Appendix 2 to Annex 2 to this Agreement.

2.	Accordingly, the temperature of the foodstuffs at any point in the load must not exceed the temperature as indicated below on loading, during carriage and on unloading.

3.	Where it is necessary to open the equipment, e.g. to carry out inspections, it is essential to ensure that the foodstuffs are not exposed to procedures or conditions contrary to the objectives of this Annex and those of the International Convention on the Harmonization of Frontier Controls of Goods.

4.	The temperature control of foodstuffs specified in this Annex should be such as not to cause freezing at any point of the load.

|  | Maximum temperature |
| --- | --- |
| I. Raw milk | + 6° C |
| II. Red meat and large game (other than red offal) | + 7o C |
| III. Meat products, pasteurized milk, fresh dairy products (yoghurt, kefir, cream and fresh cheese), ready cooked foodstuffs (meat, fish, vegetables), ready to eat prepared raw vegetables and vegetable products and fish products3 not listed below | either at + 6o C or at temperature indicated on the label and/or on the transport documents |
| IV. Game (other than large game), poultry2 and rabbits | + 4o C |
| V. Red offal2 | + 3o C |
| VI. Minced meat2 | either at +2o C or at temperature indicated on the label and/or on the transport documents |
| VII. Untreated fish, molluscs and crustaceans | on melting ice or at temperature of melting ice |

If however one should proceed to the verification of the temperature of the foodstuff, this shall be done according to the procedure laid down in Appendix 2 of Annex 2 to this agreement.

? 	When milk is collected from the farm for immediate processing, the temperature may rise during carriage to + 10o C.

Any preparations thereof.

Except for products fully treated by salting, smoking, drying or sterilization.

‘Fresh cheese’ means a non-ripened (non-matured) cheese which is ready for consumption shortly after manufacturing and which has a limited conservation period.

Raw vegetables which have been diced, sliced or otherwise size reduced, but excluding those which have only been washed, peeled or simply cut in half.

Except for live fish, live molluscs and live crustaceans.”

____________________

?/	Wagons, lorries, trailers, semi-trailers, containers and other similar equipment.

?/	In the case of tank equipment, the term "body" means under this definition, the tank itself.

/     */	To prevent frosting.

/	1/	The deep-frozen and frozen foodstuffs listed, when intended for immediate further processing at destination, may be permitted gradually to rise in temperature during carriage so as to arrive at their destination at temperatures no higher than those specified by the sender and indicated in the transport contract.  This temperature should not be higher than the maximum temperature authorized for the same foodstuff when refrigerated as mentioned in annex 3.  The transport document shall state the name of the foodstuff, whether it is deep-frozen or frozen and that it is immediately to be further processed at destination.  This carriage shall be undertaken with ATP-approved equipment without use of a thermal appliance to increase the temperature of the foodstuffs.

/	1/	The procedure will be defined.

See the following European Standards:

- EN 13485: Thermometer for measuring the air and product temperature for transport, storage and distribution of chilled, frozen, quick frozen foods and ice cream - tests, performance and suitability; and

- EN 13486: Temperature recorders and thermometers for transport, storage etc. - periodic verification.