| UNITED NATIONS |  | E |
| --- | --- | --- |
|  | Economic and Social Council | Distr. GENERAL ECE/TRANS/WP.11/218/Add.1 18 December 2008 ENGLISH Original: ENGLISH AND FRENCH |

ECONOMIC COMMISSION FOR EUROPE

INLAND TRANSPORT COMMITTEE

Working Party on the Transport of Perishable Foodstuffs

REPORT OF THE WORKING PARTY ON THE TRANSPORT OF PERISHABLE FOODSTUFFS ON ITS SIXTY-FOURTH SESSION

(14-17 October 2008)

Addendum

Revised text of Annex 1 to ATP

The secretariat reproduces below the draft revised text of Annex 1 to ATP as adopted by the Working Party at its sixty-fourth session.

*	*	*

Annex l

DEFINITIONS OF AND STANDARDS FOR SPECIAL EQUIPMENT

FOR THE CARRIAGE OF PERISHABLE FOODSTUFFS

1.	Insulated equipment.  Equipment of which the body 2 is built with insulating walls, doors, floor and roof, by which heat exchanges between the inside and outside of the body can be so limited that the overall coefficient of heat transfer (K coefficient), is such that the equipment is assignable to one or other of the following two categories:

IN   =Normally insulated equipment				-	specified by a K coefficient equal to or less than 0.70 W/m2.K;

IR   =	Heavily insulated equipment

specified by: 						-	a K coefficient equal to or less than 0.40 W/m2.K and by

-	side-walls with a thickness of at least 45 mm for transport equipment of a width greater than 2.50 m.

The definition of the K coefficient and a description of the method to be used in measuring it, are given in appendix 2 to this annex.

2.	Refrigerated equipment.  Insulated equipment which, using a source of cold (natural ice, with or without the addition of salt; eutectic plates; dry ice, with or without sublimation control; liquefied gases, with or without evaporation control, etc.) other than a mechanical or "absorption" unit, is capable, with a mean outside temperature of + 30 °C, of lowering the temperature inside the empty body to, and thereafter maintaining it:

At	+ 7 °C	maximum in the case of class A;

At 	- 10 °C	maximum in the case of class B;

At	- 20 °C	maximum in the case of class C; and

At	   0 °C		maximum in the case of class D.

If such equipment includes one or more compartments, receptacles or tanks for the refrigerant. The said compartments, receptacles or tanks shall:

Be capable of being filled or refilled from the outside; and

Have a capacity in conformity with the provisions of annex l, appendix 2, paragraph 3.1.3.

The K coefficient of refrigerated equipment of classes B and C shall in every case be equal to or less than 0.40 W/m2.K.

3.	Mechanically refrigerated equipment.  Insulated equipment either fitted with its own refrigerating appliance, or served jointly with other units of transport equipment by such an appliance, (fitted with either a mechanical compressor, or an "absorption" device, etc.).  The appliance shall be capable, with a mean outside temperature of + 30 °C, of lowering the temperature Ti inside the empty body to, and thereafter maintaining it continuously in the following manner at:

In the case of classes A, B and C, any desired practically constant inside temperature Ti in conformity with the standards defined below for the three classes:

Class A.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti may be chosen between + 12 °C and 0 °C inclusive;

Class B.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti   may be chosen between + 12 °C and - 10 °C inclusive;

Class C.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti may be chosen between + 12 °C and - 20 °C inclusive.

In the case of classes D, E and F a fixed practically constant inside temperature Ti in conformity with the standards defined below for the three classes:

Class D.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti is equal to or less than 0 °C;

Class E.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti is equal to or less than - 10 °C;

Class F.  Mechanically refrigerated equipment fitted with a refrigerating appliance such that Ti is equal to or less than - 20 °C.  The K coefficient of equipment of classes B, C, E and F shall in every case be equal to or less than 0.40 W/m2.K.

4.	Heated equipment.  Insulated equipment, which is capable of raising the inside temperature of the empty body to, and thereafter maintaining it for not less than 12 hours without renewal of supply at, a practically constant value of not less than + 12 °C when the mean outside temperature, as indicated below:

-10 °C in the case of class A heated equipment;

-20 °C in the case of class B heated equipment.

Heat producing appliances shall have a capacity in conformity with the provisions of annex 1, appendix 2, paragraphs 3.3.1 to 3.3.5.

The K coefficient of equipment of class B shall in every case be equal to or less than 0.40 W/m2.K.

# Annex 1, Appendix 1

PROVISIONS RELATING TO THE CHECKING OF INSULATED, REFRIGERATED, MECHANICALLY REFRIGERATED OR HEATED EQUIPMENT

FOR COMPLIANCE WITH THE STANDARDS

1.	Checks for conformity with the standards prescribed in this annex shall be made:

(a)	before equipment enters into service;

(b)	periodically, at least once every six years;

(c)	whenever required by the competent authority.

Except in the cases provided for in appendix 2, sections 5 and 6, to this annex, the checks shall be made at a testing station designated or approved by the competent authority of the country in which the equipment is registered or recorded, unless, in the case of the check referred to in (a) above, a check has already been made on the equipment itself or on its prototype in a testing station designated or approved by the competent authority of the country in which the equipment was manufactured.

2. 	The methods and procedures to be used in checking for compliance with the standards are described in appendix 2 to this annex.

3. 	A certificate of compliance with the standards shall be issued by the competent authority of the country in which the equipment is to be registered and recorded on a form conforming to the model reproduced in appendix 3 to this annex.

In the case of equipment transferred to another country which is a Contracting Party to ATP it shall be accompanied by the following documents so that the competent authority of the country in which the equipment is to be registered or recorded shall issue an ATP certificate:

(a)	in all cases, the test report - of the equipment itself or, in the case of serially produced equipment, of the reference equipment;

(b)	in all cases, the ATP certificate issued by the competent authority of the country of manufacture or, for equipment in service, the competent authority of the country of registration.  This certificate will be treated as a provisional certificate valid, if necessary, for three months;

(c)	in the case of serially produced equipment, the technical specification of the equipment to be certified as issued by the manufacturer of the equipment or his duly accredited representative (this specification shall cover the same items as the descriptive pages concerning the equipment which appear in the test report and shall be drawn up in at least one of the three official languages).

In the case of equipment transferred after it has been in use, the equipment may be subject to a visual inspection to confirm its identity before the competent authority of the country in which it is to be registered or recorded issues a certificate of compliance.  The certificate or a certified true photographic copy thereof shall be carried on the equipment during carriage and be produced whenever so required by the control authorities.  However, if a certification plate, as reproduced in appendix 3 to this annex, is fixed to the equipment, the ATP plate shall be recognized as equivalent to an ATP certificate. ATP certification plates shall be removed as soon as the equipment ceased to conform to the standards laid down in this annex.

4.	Distinguishing marks and particulars shall be affixed to the equipment in conformity with the provisions of appendix 4 to this annex.  They shall be removed as soon as the equipment ceases to conform to the standards laid down in this annex.

5. 	The insulated bodies of "insulated", "refrigerated", "mechanically refrigerated" or "heated" transport equipment and their thermal appliances shall each bear a durable manufacturer’s plate firmly affixed by the manufacturer in a conspicuous and readily accessible position on a part not subject to replacement in use. It shall be able to be checked easily and without the use of tools.  For insulated bodies, the manufacturer’s plate shall be on the outside of the body.  The manufacturer’s plate shall show clearly and indelibly at least the following particulars:

Country of manufacture or letters used in international road traffic;

Name of manufacturer or company;

Model (figures and/or letters);

Serial number;

Month and year of manufacture.

6. 	(a)	New equipment of a specific type serially produced may be approved by testing one unit of that type.  If the unit tested meets class specification, the resulting test report shall be regarded as a Type Approval Certificate.  This certificate shall expire at the end of a period of six years beginning from the date of completion of the test.

The date of expiry of test reports shall be stated in months and years.

(b)	The competent authority shall take steps to verify that production of other units is in conformity with the approved type.  For this purpose it may check by testing sample units drawn at random from the production series.

(c)	A unit shall not be regarded as being of the same type as the unit tested unless it satisfies the following minimum conditions:

(i)	If it is insulated equipment, in which case the reference equipment may be insulated, refrigerated, mechanically refrigerated or heated equipment,

the construction shall be comparable and, in particular, the insulating material and the method of insulation shall be identical;

the thickness of the insulating material shall be not less than that of the reference equipment;

the interior fittings shall be identical or simplified;

the number of doors and the number of hatches or other openings shall be the same or less; and

the inside surface area of the body shall not be as much as 20% greater or smaller;

(ii)	If it is refrigerated equipment, in which case the reference equipment shall be refrigerated equipment,

the conditions set out under (i) above shall be satisfied;

inside circulating fans shall be comparable;

the source of cold shall be identical; and

the reserve of cold per unit of inside surface area shall be greater or equal;

(iii)	If it is mechanically refrigerated equipment, in which case the reference equipment shall be either:

(a)	mechanically refrigerated equipment;

-	the conditions set out in (i) above shall be satisfied; and

-	the effective refrigerating capacity of the mechanical refrigeration appliance per unit of inside surface area, under the same temperature conditions, shall be greater or equal;

or	(b)	insulated equipment to which is complete in every detail but minus its mechanical refrigeration unit which will be fitted at a later date.

The resulting aperture will be filled, during the measurement of the K coefficient, with close fitting panels of the same overall thickness and type of insulation as is fitted to the front wall.  In which case:

-	the conditions set out in (i) above shall be satisfied; and

-	the effective refrigerating capacity of the mechanical refrigeration unit fitted to insulated reference equipment shall be as defined in annex 1, appendix 2, paragraph 3.2.6.

(iv)	If it is heated equipment, in which case the reference equipment may be insulated or heated equipment,

-	the conditions set out under (i) above shall be satisfied;

-	the source of heat shall be identical; and

-	the capacity of the heating appliance per unit of inside surface area shall be greater or equal.

(d)	If, in the course of the six-year period, the production series exceeds 100 units, the competent authority shall determine the percentage of units to be tested.

# Annex l, Appendix 2

METHODS AND PROCEDURES FOR MEASURING AND CHECKING THE INSULATING CAPACITY AND THE EFFICIENCY OF THE COOLING OR HEATING APPLIANCES OF SPECIAL EQUIPMENT FOR

THE CARRIAGE OF PERISHABLE FOODSTUFFS

## 1.	DEFINITIONS AND GENERAL PRINCIPLES

1.1	K coefficient.  The overall heat transfer coefficient (K coefficient) of the special equipment is defined by the following formula:

K  =  WS .ΔT

where W is either the heating power or the cooling capacity, as the case may be, required to maintain a constant absolute temperature difference T between the mean inside temperature Ti and the mean outside temperature Te, during continuous operation, when the mean outside temperature Te is constant for a body of mean surface area S.

1.2	The mean surface area S of the body is the geometric mean of the inside surface area Si and the outside surface area Se of the body:

S  =  Si.Se

In determining the two surface areas Si and Se, structural peculiarities and surface irregularities of the body, such as chamfers, wheel-arches and similar features, shall be taken into account and shall be noted under the appropriate heading in test reports; however, if the body is covered with corrugated sheet metal the area considered shall be that of the plane surface occupied, not that of the developed corrugated surface.

Temperature measuring points

1.3	In the case of parallelepipedic bodies, the mean inside temperature of the body (Ti) is the arithmetic mean of the temperatures measured 10 cm from the walls at the following 12 points:

(a)	The eight inside corners of the body; and

(b)	The centres of the four inside faces having the largest area.

If the body is not parallelepipedic, the 12 points of measurements shall be distributed as satisfactorily as possible having regard to the shape of the body.

1.4 	In the case of parallelepipedic bodies, the mean outside temperature of the body (Te) is the arithmetic mean of the temperatures measured 10 cm from the walls at the following 12 points:

(a)	The eight outside corners of the body; and

(b)	The centres of the four outside faces having the largest area.

If the body is not parallelepipedic, the 12 points of measurement shall be distributed as satisfactorily as possible having regard to the shape of the body.

1.5 	The mean temperature of the walls of the body is the arithmetic mean of the mean outside temperature of the body and the mean inside temperature of the body:

Te + Ti2

1.6	Temperature measuring instruments protected against radiation shall be placed inside and outside the body at the points specified in paragraphs 1.3 and 1.4 of this appendix.

Steady state period and duration of test

1.7 	The mean outside temperatures and the mean inside temperatures of the body, taken over a steady period of not less than 12 hours, shall not vary by more than ± 0.3 K, and these temperatures shall not vary by more than ± 1.0 K during the preceding 6 hours.

The difference between the heating power or cooling capacity measured over two periods of not less than 3 hours at the start and at the end of the steady state period, and separated by at least 6 hours, shall be less than 3 %.

The mean values of the temperatures and heating or cooling capacity over at least the last 6 hours of the steady state period will be used in K coefficient calculation.

The mean inside and outside temperatures at the beginning and the end of the calculation period of at least 6 hours shall not differ by more that 0.2 K.

2.	INSULATING CAPACITY OF EQUIPMENT

Procedures for measuring the K coefficient

2.1	Equipment other than liquid-foodstuffs tanks

2.1.1 	K coefficient shall be measured in continuous operation either by the internal cooling method or by the internal heating method. In either case, the empty body shall be placed in an insulated chamber.

Test Method

2.1.2	Where the internal cooling method is used, one or more heat exchangers shall be placed inside the body.  The surface area of these exchangers shall be such that, if a fluid at a temperature not lower than 0 °C */ passes through them, the mean inside temperature of the body remains below + 10 °C when continuous operation has been established.  Where the internal heating method is used, electrical heating appliances (resistors, etc.) shall be used.  The heat exchangers or electrical heating appliances shall be fitted with fans having a delivery rate sufficient to obtain 40 to 70 air charges per hour related to the empty volume of the tested body, and the air distribution around all inside surfaces of the tested body shall be sufficient to ensure that the maximum difference between the temperatures of any 2 of the 12 points specified in paragraph 1.3 of this appendix does not exceed 2 K when continuous operation has been established.

2.1.3 	Heat quantity:	The heat dissipated by the electrical resistance fan heaters shall not exceed a flow of 1W/cm2 and the heater units shall be protected by a casing of low emissivity.

The electrical energy consumption shall be determined with an accuracy of 0.5%.

Test Procedure

2.1.4	Whatever the method employed, the mean temperature of the insulated chamber shall throughout the test be kept uniform, and constant in compliance with paragraph 1.7 of this appendix, to within ± 0.5 K, at a level such that the temperature difference between the inside of the body and the insulated chamber is 25 °C ± 2 K, the average temperature of the walls of the body being maintained at + 20 °C ± 0.5 K.

2.1.5	During the test, whether by the internal cooling method or by the internal heating method, the mass of air in the chamber shall be made to circulate continuously so that the speed of movement of the air 10 cm from the walls is maintained at between l and 2 metres/second.

2.1.6	The appliances for generating and distributing cold or heat and for measuring the quantity of cold or heat exchanged and the heat equivalent of the air-circulating fans shall be started up.  Electrical cable losses between the heat input measuring instrument and the tested body shall be established by a measurement or calculation and subtracted from the total heat input measured.

2.1.7	When continuous operation has been established, the maximum difference between the temperatures at the warmest and at the coldest points on the outside of the body shall not exceed 2 K.

2.1.8	The mean outside temperature and the mean inside temperature of the body shall each be read not less than four times per hour.

2.2	Liquid-foodstuffs tanks

2.2.1	The method described below applies only to single-compartment or multiple-compartment tank equipment intended solely for the carriage of liquid foodstuffs such as milk.  Each compartment of such tanks shall have at least one manhole and one discharge-pipe connecting socket; where there are several compartments they shall be separated from one another by non-insulated vertical partitions.

2.2.2	K coefficients shall be measured in continuous operation by internal heating of the empty tank in an insulated chamber.

Test method

2.2.3	An electrical heating appliance (resistors, etc.) shall be placed inside the tank.  If the tank has several compartments, an electrical heating appliance shall be placed in each compartment.  The electrical heating appliances shall be fitted with fans with a delivery rate sufficient to ensure that the difference between the maximum temperature and the minimum temperature inside each compartment does not exceed 3 K when continuous operation has been established.  If the tank comprises several compartments, the difference between the mean temperature in the coldest compartment and the mean temperature in the warmest compartment shall not exceed 2 K, the temperatures being measured as specified in paragraph 2.2.4 of this appendix.

2.2.4	Temperature measuring instruments protected against radiation shall be placed inside and outside the tank 10 cm from the walls, as follows:

(a)	If the tank has only one compartment, measurements shall be made at a minimum of 12 points positioned as follows:

The four extremities of two diameters at right angles to one another, one horizontal and the other vertical, near each of the two ends of the tank;

The four extremities of two diameters at right angles to one another, inclined at an angle of 45° to the horizontal, in the axial plane of the tank;

(b)	If the tank has several compartments, the points of measurement shall be as follows:

for each of the two end compartments, at least the following:

The extremities of a horizontal diameter near the end and the extremities of a vertical diameter near the partition;

and for each of the other compartments, at least the following:

The extremities of a diameter inclined at an angle of 45° to the horizontal near one of the partitions and the extremities of a diameter perpendicular to the first and near the other partition.

The mean inside temperature and the mean outside temperature of the tank shall respectively be the arithmetic mean of all the measurements taken inside and all the measurements taken outside the tank.  In the case of a tank having several compartments, the mean inside temperature of each compartment shall be the arithmetic mean of the measurements, numbering not less than four, relating to that compartment.

Test procedure

2.2.5	Throughout the test, the mean temperature of the insulated chamber shall be kept uniform, and constant in compliance with paragraph 1.7 of this appendix, at a level such that the difference in temperature between the inside of the tank and that of the insulated chamber is not less than 25 °C ± 2 K, with the average temperature of the tank walls being maintained at + 20 °C ± 0.5 K.

2.2.6	The mass of air in the chamber shall be made to circulate continuously so that the speed of movement of the air 10 cm from the walls is maintained at between l and 2 metres/second.

2.2.7	The appliances for heating and circulating the air and for measuring the quantity of heat exchanged and the heat equivalent of the air-circulating fans shall be started up.

2.2.8	When continuous operation has been established, the maximum difference between the temperatures at the warmest and at the coldest points on the outside of the tank shall not exceed 2 K.

2.2.9	The mean outside temperature and the mean inside temperature of the tank shall each be read not less than four times per hour.

2.3	Provisions common to all types of insulated equipment

2.3.1	Verification of the K coefficient

Where the purpose of the tests is not to determine the K coefficient but simply to verify that it is below a certain limit, the tests carried out as described in paragraphs 2.1.1. to 2.2.9 of this appendix may be stopped as soon as the measurements made show that the K coefficient meets the requirements.

2.3.2	Accuracy of measurements of the K coefficient

Testing stations shall be provided with the equipment and instruments necessary to ensure that the K coefficient is determined with a maximum margin of error of ± 10% when using the method of internal cooling and ± 5% when using the method of internal heating.

3.	EFFECTIVENESS OF THERMAL APPLIANCES OF EQUIPMENT

### Procedures for determining the efficiency of thermal appliances of equipment

3.1	Refrigerated equipment

3.1.1	The empty equipment shall be placed in an insulated chamber whose mean temperature shall be kept uniform, and constant to within ± 0.5 K, at + 30 °C.  The mass of air in the chamber shall be made to circulate as described in paragraph 2.1.5 of this appendix.

3.1.2	Temperature measuring instruments protected against radiation shall be placed inside and outside the body at the points specified in paragraphs 1.3 and 1.4 of this appendix.

Test procedure

3.1.3	(a)	In the case of equipment other than equipment with fixed eutectic plates, and equipment fitted with liquefied gas systems, the maximum weight of refrigerant specified by the manufacturer or which can normally be accommodated shall be loaded into the spaces provided when the mean inside temperature of the body has reached the mean outside temperature of the body (+ 30 °C).  Doors, hatches and other openings shall be closed and the inside ventilation appliances (if any) of the equipment shall be started up at maximum capacity.  In addition, in the case of new equipment, a heating appliance with a heating capacity equal to 35% of the heat exchanged through the walls in continuous operation shall be started up inside the body when the temperature prescribed for the class to which the equipment is presumed to belong has been reached.  No additional refrigerant shall be loaded during the test;

(b)	In the case of equipment with fixed eutectic plates, the test shall comprise a preliminary phase of freezing of the eutectic solution.  For this purpose, when the mean inside temperature of the body and the temperature of the plates have reached the mean outside temperature (+ 30 °C), the plate-cooling appliance shall be put into operation for 18 consecutive hours after closure of the doors and hatches.  If the plate-cooling appliance includes a cyclically-operating mechanism, the total duration of operation of the appliance shall be 24 hours.  In the case of new equipment, as soon as the cooling appliance is stopped, a heating appliance with a heating capacity equal to 35% of the heat exchanged through the walls in continuous operation shall be started up inside the body when the temperature prescribed for the class to which the equipment is presumed to belong has been reached.  The solution shall not be subjected to any re-freezing operation during the test;

(c)	In the case of equipment fitted with liquefied gas systems, the following test procedure shall be used:  when the mean inside temperature of the body has reached the mean outside temperature (+ 30 °C), the receptacles for the liquefied gas shall be filled to the level prescribed by the manufacturer.  Then the doors, hatches and other openings shall be closed as in normal operation and the inside ventilation appliances (if any) of the equipment shall be started up at maximum capacity.  The thermostat shall be set at a temperature not more than 2 degrees below the limit temperature of the presumed class of the equipment.  Cooling of the body then shall be commenced.  During the cooling of the body the refrigerant consumed is simultaneously replaced.  This replacement shall be effected:

Either for a time corresponding to the interval between the commencement of cooling and the moment when the temperature prescribed for the class to which the equipment is presumed to belong is reached for the first time; or

For a duration of three hours counting from the commencement of cooling, whichever is shorter.

Beyond this period, no additional refrigerant shall be loaded during the test.

In the case of new equipment, a heating appliance with a heating capacity equal to 35% of the heat exchanged through the walls in continuous operation shall be started up inside the body when the class temperature has been reached.

Provisions common to all types of refrigerated equipment

3.1.4	The mean outside temperature and the mean inside temperature of the body shall each be read not less often than once every 30 minutes.

3.1.5	The test shall be continued for 12 hours after the mean inside temperature of the body has reached the lower limit prescribed for the class to which the equipment is presumed to belong (A = + 7 °C; B = - 10 °C; C = - 20 °C; D = 0 °C) or, in the case of equipment with fixed eutectic plates, after stoppage of the cooling appliance.

Criterion of satisfaction

3.1.6	The test shall be deemed satisfactory if the mean inside temperature of the body does not exceed the aforesaid lower limit during the aforesaid period of 12 hours.

### 3.2	Mechanically refrigerated equipment

Test method

3.2.1	The test shall be carried out in the conditions described in paragraphs 3.1.1 and 3.1.2 of this appendix.

Test procedure

3.2.2	When the mean inside temperature of the body reaches the outside temperature (+ 30 °C), the doors, hatches and other openings shall be closed and the refrigerating appliance and the inside ventilating appliances (if any) shall be started up at maximum capacity.  In addition, in the case of new equipment, a heating appliance with a heating capacity equal to 35% of the heat exchanged through the walls in continuous operation shall be started up inside the body when the temperature prescribed for the class to which the equipment is presumed to belong has been reached.

3.2.3	The mean outside temperature and the mean inside temperature of the body shall each be read not less often than once every 30 minutes.

3.2.4	The test shall be continued for 12 hours after the mean inside temperature of the body has reached:

Either the lower limit prescribed for the class to which the equipment is presumed to belong in the case of classes A, B and C (A = 0 °C; B = - 10 °C; C = - 20 °C); or

A level not lower than the upper limit prescribed for the class to which the equipment is presumed to belong in the case of classes D, E, and F (D = 0 °C; E = - 10 °C; F = - 20 °C).

Criterion of satisfaction

3.2.5	The test shall be deemed satisfactory if the refrigerating appliance is able to maintain the prescribed temperature conditions during the said 12-hour periods, with any automatic defrosting of the refrigerating unit not being taken into account.

3.2.6	If the refrigerating appliance with all its accessories has undergone separately, to the satisfaction of the competent authority, a test to determine its effective refrigerating capacity at the prescribed reference temperatures, the transport equipment may be accepted as mechanically refrigerated equipment without undergoing an efficiency test if the effective refrigerating capacity of the appliance in continuous operation exceeds the heat loss through the walls for the class under consideration, multiplied by the factor l.75.

3.2.7	If the mechanically refrigerating unit is replaced by a unit of a different type, the competent authority may:

(a)	require the equipment to undergo the determinations and verifications prescribed in paragraphs 3.2.1 to 3.2.4; or

(b)	satisfy itself that the effective refrigerating capacity of the new mechanically refrigerating unit is, at the temperature prescribed for equipment of the class concerned, at least equal to that of the unit replaced; or

(c)	satisfy itself that the effective refrigerating capacity of the new mechanically refrigerating unit meets the requirements of paragraph 3.2.6.

### 3.3	Heated equipment

Test method

3.3.1	The empty equipment shall be placed in an insulated chamber whose temperature shall be kept uniform and constant at as low a level as possible.  The atmosphere of the chamber shall be made to circulate as described in paragraph 2.1.5 of this appendix.

3.3.2	Temperature measuring instruments protected against radiation shall be placed inside and outside the body at the points specified in paragraphs 1.3 and 1.4 of this appendix.

Test procedure

3.3.3	Doors, hatches and other openings shall be closed and the heating equipment and the inside ventilating appliances (if any) shall be started up at maximum capacity.

3.3.4	The mean outside temperature and the mean inside temperature of the body shall each be read not less often than once every 30 minutes.

3.3.5	The test shall be continued for 12 hours after the difference between the mean inside temperature and the mean outside temperature of the body has reached the level corresponding to the conditions prescribed for the class to which the equipment is presumed to belong. In the case of new equipment, the above temperature difference shall be increased by 35 per cent.

Criterion of satisfaction

3.3.6	The test shall be deemed satisfactory if the heating appliance is able to maintain the prescribed temperature difference during the 12 hours aforesaid.

4.	Procedure for measuring the effective refrigerating capacity Wo of a unit when the evaporator is free from frost

4.1	General principles

4.1.1	When attached to either a calorimeter box or the insulated body of a unit of transport equipment, and operating continuously, this capacity is:

Wo=Wj + U. T

where U is the heat leakage of the calorimeter box or insulated body, Watts/°C.

T is the difference between the mean inside temperature Ti and the mean outside temperature Te of the calorimeter or insulated body (K),

Wj is the heat dissipated by the fan heater unit to maintain each temperature difference in equilibrium.

4.2	Test method

4.2.1	The refrigeration unit is either fitted to a calorimeter box, or the insulated body of a unit of transport equipment.

In each case, the heat leakage is measured at a single mean wall temperature prior to the capacity test.  An arithmetical correction factor, based upon the experience of the testing station, is made to take into account the average temperature of the walls at each thermal equilibrium during the determination of the effective refrigerating capacity.

It is preferable to use a calibrated calorimeter box to obtain maximum accuracy.

Measurements and procedure shall be as described in paragraphs 1.1 to 2.1.8 above; however, it is sufficient to measure U the heat leakage only, the value of this coefficient being defined by the following relationship:

U=WΔTm

where:

W	is the heating power (in watts) dissipated by the internal heater and fans;

ΔTm	is the difference between the mean internal temperature Ti and the mean external temperature Te;

U	is the heat flow per degree of difference between the air temperature inside and outside the calorimeter box or unit of transport equipment measured with the refrigeration unit fitted.

The calorimeter box or unit of transport equipment is placed in a test chamber.  If a calorimeter box is used, U.ΔT should be not more than 35% of the total heat flow Wo.

The calorimeter box or unit of transport equipment shall be heavily insulated.

4.2.2 	Instrumentation

Test stations shall be equipped with instruments to measure the U value to an accuracy of ± 5%.  Heat transfer through air leakage should not exceed 5% of the total heat transfer through the calorimeter box or through the insulated body of the unit of transport equipment. The refrigerating capacity shall be determined with an accuracy of ± 5%.

The instrumentation of the calorimeter box or unit of transport equipment shall conform to paragraphs 4 1.3 and 1.4 above.  The following are to be measured:

(a)	Air temperatures:	At least four thermometers uniformly distributed at the inlet to the evaporator;

At least four thermometers uniformly distributed at the outlet to the evaporator;

At least four thermometers uniformly distributed at the air inlet(s) to the refrigeration unit;

The thermometers shall be protected against radiation.

The accuracy of the temperature measuring system shall be 0.2 K;

(b)	Energy consumption:	Instruments shall be provided to measure the electrical energy or fuel consumption of the refrigeration unit.

The electrical energy and fuel consumption shall be determined with an accuracy of 0.5%;

(c)	Speed of rotation:	Instruments shall be provided to measure the speed of rotation of the compressors and circulating fans or to allow these speeds to be calculated where direct measurement is impractical.

The speed of rotation shall be measured to an accuracy of 1%;

(d)	Pressure:	High precision pressure gauges (accurate to ± 1%) shall be fitted to the condenser and evaporator and to the compressor inlet when the evaporator is fitted with a pressure regulator.

4.2.3 	Test conditions

(i)	The average air temperature at the inlet(s) to the refrigeration unit shall be maintained at 30 °C + 0.5 K.

The maximum difference between the temperatures at the warmest and at the coldest points shall not exceed 2 K.

(ii)	Inside the calorimeter box or the insulated body of the unit of transport equipment (at the air inlet to the evaporator):  there shall be three levels of temperature between -25 °C and +12 °C depending on the characteristics of the unit, one temperature level being at the minimum prescribed for the class requested by the manufacturer with a tolerance of ± 1 K.

The mean inside temperature shall be maintained within a tolerance of ± 0.5 K.  During the measurement of refrigerating capacity, the heat dissipated within the calorimeter box or the insulated body of the unit of transport equipment shall be maintained at a constant level with a tolerance of ± 1%.

When presenting a refrigeration unit for test, the manufacturer shall supply:

-	Documents describing the unit to be tested;

-	A technical document outlining the parameters that are most important to the functioning of the unit and specifying their allowable range;

-	The characteristics of the equipment series tested; and

-	A statement as to which prime mover(s) shall be used during testing.

4.3	Test procedure

4.3.1	The test shall be divided into two major parts, the cooling phase and the measurement of the effective refrigerating capacity at three increasing temperature levels.

(a)	Cooling phase; the initial temperature of the calorimeter box or transport equipment shall be 30 ºC ± 3 K. It shall then be lowered to the following temperatures: -25 ºC for -20 ºC class, -13 ºC for -10 ºC class or -2 ºC for 0 ºC class;

(b)	Measurement of effective refrigerating capacity, at each internal temperature level.

A first test to be carried out, for at least four hours at each level of temperature, under control of the thermostat (of the refrigeration unit) to stabilize the heat transfer between the interior and exterior of the calorimeter box or unit of transport equipment.

A second test shall be carried out without the thermostat in operation in order to determine the maximum refrigerating capacity, with the heating power of the internal heater producing an equilibrium condition at each temperature level as prescribed in paragraph 4.2.3.

The duration of the second test shall be not less than four hours.

Before changing from one temperature level to another, the box or unit shall be manually defrosted.

If the refrigeration unit can be operated by more than one form of energy, the tests shall be repeated accordingly.

If the compressor is driven by the vehicle engine, the test shall be carried out at both the minimum speed and at the nominal speed of rotation of the compressor as specified by the manufacturer.

If the compressor is driven by the vehicle motion, the test shall be carried out at the nominal speed of rotation of the compressor as specified by the manufacturer.

4.3.2	The same procedure shall be followed for the enthalpy method described below, but in this case the heat power dissipated by the evaporator fans at each temperature level shall also be measured.

This method may, alternatively, be used to test reference equipment. In this case, the effective refrigerating capacity is measured by multiplying the mass flow (m) of the refrigerant liquid by the difference in enthalpy between the refrigerant vapour leaving the unit (ho) and the liquid at the inlet to the unit (hi).

To obtain the effective refrigerating capacity, the heat generated by the evaporator fans (Wf) is deducted.  It is difficult to measure Wf if the evaporator fans are driven by an external motor, in this particular case the enthalpy method is not recommended.  When the fans are driven by internal electric motors, the electrical power is measured by appropriate instruments with an accuracy of ± 3%, with refrigerant flow measurement being accurate to ± 3%.

The heat balance is given by the formula:

Wo = (ho - hi) m - Wf.

Appropriate methods are described in standards ISO 971, BS 3122, DIN, NEN, etc.  An electric heater is placed inside the equipment in order to obtain the thermal equilibrium.

4.3.3	Precautions

As the tests for effective refrigerating capacity are carried out with the thermostat of the refrigeration unit disconnected, the following precautions shall be observed:

If the equipment has a hot gas injection system, it shall be inoperative during the test;

with automatic controls of the refrigeration unit which unload individual cylinders (to tune the capacity of the refrigeration unit to motor output) the test shall be carried out with the number of cylinders appropriate for the temperature.

4.3.4	Checks

The following should be verified and the methods used indicated on the test report:

(i)	the defrosting system and the thermostat are functioning correctly;

(ii)	the rate of air circulation is that specified by the manufacturer.

If the air circulation of a refrigeration unit’s evaporator fans is to be measured, methods capable of measuring the total delivery volume shall be used. Use of one of the relevant existing standards, i.e. BS 848, ISO 5801, AMCA 210-85, DIN 24163, NFE 36101, NF X10.102, DIN 4796 is recommended;

(iii)	the refrigerant used for tests is that specified by the manufacturer.

4.4	Test result

4.4.1	The refrigeration capacity for ATP purposes is that relating to the mean temperature at the inlet(s) of the evaporator.  The temperature measuring instruments shall be protected against radiation.

5.	Checking the insulating capacity of equipment in service

For the purpose of checking the insulating capacity of each piece of equipment in service as prescribed in appendix 1, paragraphs l (b) and 1 (c), to this annex, the competent authorities may:

Apply the methods described in paragraphs 2.1.1 to 2.3.2 of this appendix; or

Appoint experts to assess the fitness of the equipment for retention in one or other of the categories of insulated equipment.  These experts shall take the following particulars into account and shall base their conclusions on information as indicated below.

5.1	General examination of the equipment

This examination shall take the form of an inspection of the equipment to determine the following:

(i)	the durable manufacturer’s plate affixed by the manufacturer;

(ii)	the general design of the insulating sheathing;

(iii)	the method of application of insulation;

(iv)	the nature and condition of the walls;

(v)	the condition of the insulated compartment;

(vi)	the thickness of the walls;

and to make all appropriate observations concerning the effective insulating capacity of the equipment. For this purpose the experts may cause parts of the equipment to be dismantled and require all documents they may need to consult (plans, test reports, specifications, invoices, etc.) to be placed at their disposal.

5.2	Examination for air-tightness (not applicable to tank equipment)

The inspection shall be made by an observer stationed inside the equipment, which shall be placed in a brightly-illuminated area.  Any method yielding more accurate results may be used.

5.3	Decisions

(i)	If the conclusions regarding the general condition of the body are favourable, the equipment may be kept in service as insulated equipment of its initial class for a further period of not more than three years.  If the conclusions of the expert or experts are not acceptable, the equipment may be kept in service only following a satisfactory measurement of K coefficient according to the procedure described in paragraphs 2.1.1 to 2.3.2 of this appendix; it may then be kept in service for a further period of six years.

- In the case of heavily insulated equipment, if the conclusions of an expert or experts show the body to be unsuitable for keeping in service in its initial class but suitable for continuing in service as normally insulated equipment, then the body may be kept in service in an appropriate class for a further three years.  In this case, the distinguishing marks (as in appendix 4 of this annex) shall be changed appropriately.

(iii)	If the equipment consists of units of serially-produced equipment of a particular type satisfying the requirements of appendix l, paragraph 6, to this annex and belonging to one owner, then in addition to an inspection of each unit of equipment the K coefficient of not less than l% of the number of units involved, may be measured in conformity with the provisions of sections 2.1, 2.2 and 2.3 of this appendix.  If the results of the examinations and measurements are acceptable, all the equipment in question may be kept in service as insulating equipment of its initial class for a further period of six years.

6.	Verifying the EFFECTIVENESS of thermal appliances of equipment in service

To verify as prescribed in appendix l, paragraphs l (b) and l (c), to this annex the effectiveness of the thermal appliance of each item of refrigerated, mechanically refrigerated or heated equipment in service, the competent authorities may:

Apply the methods described in sections 3.1, 3.2 and 3.3 of this appendix; or

Appoint experts to apply the particulars described in sections 5.1 and 5.2 of this annex when appropriate as well as the following provisions:

6.1	Refrigerated equipment other than equipment with fixed eutectic accumulators

It shall be verified that the inside temperature of the empty equipment, previously brought to the outside temperature, can be brought to the limit temperature of the class to which the equipment belongs, as prescribed in this annex, and maintained below the said limit temperature for a period t

such that t≥12ΔTΔT'	in which

ΔT is the difference between + 30 °C and the said limit temperature, and

ΔT' is the difference between the mean outside temperature during the test and the class limit temperature, the outside temperature being not lower than + 15 °C.

If the results are acceptable, the equipment may be kept in service as refrigerated equipment of its initial class for a further period of not more than three years.

6.2	Mechanically refrigerated equipment

(i)	Equipment constructed one year after the entry into force of these provisions [DD MM YYYY]

Checks shall be made to ensure that, when the outside temperature is not lower than + 15 °C, the inside temperature of the empty equipment, which has been previously equalized to that outside, can be reduced to the required class temperature within a maximum period (in minutes), as prescribed in the table below:

| Outside temperature | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | °C |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Class C, F | 360 | 350 | 340 | 330 | 320 | 310 | 300 | 290 | 280 | 270 | 260 | 250 | 240 | 230 | 220 | 210 | min |
| Class B, E | 270 | 262 | 253 | 245 | 236 | 228 | 219 | 211 | 202 | 194 | 185 | 177 | 168 | 160 | 151 | 143 | min |
| Class A, D | 180 | 173 | 166 | 159 | 152 | 145 | 138 | 131 | 124 | 117 | 110 | 103 | 96 | 89 | 82 | 75 | min |

The inside temperature of the empty equipment must have been previously brought to the outside temperature.

If the results are favourable, the equipment may be kept in service as mechanically refrigerated equipment of its initial class for a further period of not more than three years.

(ii)	Transitional provisions applicable to equipment in service

For equipment constructed prior to the entry into force of these provisions [DD MM YYYY], the following provisions shall apply:

It shall be verified that, when the outside temperature is not lower than +15° C, the inside temperature of the empty equipment, which has been previously brought to the outside temperature, can be brought within a maximum period of six hours:

In the case of equipment in classes A, B or C, to the minimum temperature, as prescribed in this annex;

In the case of equipment in classes D, E or F, to the limit temperature, as prescribed in this annex.

If the results are acceptable, the equipment may be kept in service as mechanically refrigerated equipment of its initial class for a further period of not more than three years.

6.3	Heated equipment

It shall be verified that the difference between the inside temperature of the equipment and the outside temperature which governs the class to which the equipment belongs as prescribed in this annex (a difference of 22 K in the case of class A and of 32 K in the case of class B) can be achieved and be maintained for not less than 12 hours.  If the results are acceptable, the equipment may be kept in service as heated equipment of its initial class for a further period of not more than three years.

6.4	Temperature measuring points

Temperature measuring points protected against radiation shall be placed inside the body and outside the body.

For measuring the inside temperature of the body (Ti), at least 2 temperature measuring points shall be placed inside the body at a maximum distance of 50cm from the front wall, 50cm from the rear door at a height of a minimum of 15 cm and a maximum of  20 cm above the floor area.

For measuring the outside temperature of the body (Te), at least 2 temperature measuring points shall be placed at a distance of at least 10 cm from an outer wall of the body and at least 20 cm from the air inlet of the condenser unit.

The final reading should be from the warmest point inside the body and the coldest point outside.

6.5	Provisions common to refrigerated, mechanically refrigerated and heated equipment

(i)	If the results are not acceptable, refrigerated, mechanically refrigerated or heated equipment may be kept in service in its initial class only if it passes at a testing station the tests described in sections 3.1, 3.2 and 3.3 of this appendix; it may then be kept in service in its initial class for a further period of six years.

(ii)	If the equipment consists of units of serially-produced refrigerated, mechanically refrigerated or heated equipment of a particular type satisfying the requirements of appendix l, paragraph 6, to this annex and belonging to one owner, then in addition to an inspection of the thermal appliances to ensure that their general condition appears to be satisfactory, the effectiveness of the cooling or heating appliances of not less than l% of the number of units may be determined at a testing station in conformity with the provisions of sections 3.1, 3.2 and 3.3 of this appendix. If the results of the examinations and of the determination of effectiveness are acceptable, all the equipment in question may be kept in service in its initial class for a further period of six years.

7.	Test Reports

A test report of the type appropriate to the equipment tested shall be drawn up for each test in conformity with one or other of the models 1 to 10 hereunder.

MODEL No. 1 A

Test Report

Prepared in conformity with the provisions of the Agreement on the International Carriage of Perishable Foodstuffs and on the Special Equipment to be Used for such Carriage (ATP)

Test report No………..

Section 1

Specifications of the equipment (equipment other than tanks for the carriage of liquid foodstuffs)

Approved testing station/expert: l/

Name ………………………………………………………………………………………………

Address …………………………………………………………………………………………….

Type of equipment: 2/

Make…………………….Registration number…………………….Serial number……………….

Date of first entry into service …………………………………………………………………….

Tare 3/………………………………………..kg      Carrying capacity 3/ ………………………kg

Body:

Make and type ………………………………	 Identification number ………………………

Built by …………………………………………………………………………………………..

Owned or operated by ……………………………………………………………………………..

Submitted by……………………………………………………………………………………….

Date of construction ……………………………………………………………………………….

Principal dimensions:

Outside: length………….	 m, width ……………	m, height………………………… m

Inside:  length ……………	 m, width …………	m, height………………………… m

Total floor area of body………………………………………………………………………. m2

Usable internal volume of body ……………………………………………………………….. m3

MODEL No. 1 A (cont'd)

Total inside surface area Si of body …………………………………………………………… m2

Total outside surface area Se of body………………………………………………………….. m2

Mean surface area:S  =  Si.Se ………………………………………………………………. m2

Specifications of the body walls: 4/

Top ………………………………………………………………………………………………..

Bottom …………………………………………………………………………………………….

Sides 	………………………………………………………………………………………………

Structural peculiarities of body: 5/

Number,) of doors …………………………………………………………………….

positions) of vents ……………………………………………………………………

and dimensions ) of ice-loading apertures	……………………………………………………

Accessories 6/ 		……………………………………………………………………………….

………………………………………………………………………………..

K coefficient = …………………………………………………………………………………W/m2.K

1/	Delete as necessary (experts only in the case of tests carried out under ATP annex 1, appendix 2, sections 5 or 6).

2/	Wagon, lorry, trailer, semi-trailer, container, etc.

3/	State source of information.

4/	Nature and thickness of materials constituting the body walls, from the interior to the exterior, mode of construction, etc.

5/	If there are surface irregularities, show how Si and Se were determined.

6/	Meat bars, flettner fans, etc.

MODEL No. 1 B

Test Report

prepared in conformity with the provisions of the Agreement on the International Carriage of Perishable Foodstuffs and on the Special Equipment to be Used for such Carriage (ATP)

Test report No……………

Section 1

Specifications of tanks for the carriage of liquid foodstuffs

Approved testing station/expert: l/

Name ……………………………………………………………………………………………

Address …………………………………………………………………………………………….

Type of tank: 2/

Make ……………..	Registration number…………………	 Serial number ………….…….

Date of first entry into service 	…………………………………………………………………..

Tare 3/ …………………………………	 kg  Carrying capacity 3/ ……………………….. kg

Tank:

Make and type ………………………..	      Identification number ………………….………

Built by …………………………………………………………………………………………….

Owned or operated by ……………………………………………………………………………..

Submitted by ………………………………………………………………………………………

Date of construction ……………………………………………………………………………….

Principal dimensions:

Outside: length of cylinder ……….	 m, major axis ……….	 m, minor axis ……………… m

Inside:  length of cylinder ………..	 m, major axis ……….	 m, minor axis ……………… m

Usable internal volume ……………………………………………………………………… m3

MODEL No. 1 B (cont'd)

Internal volume of each compartment ………………………………………………………… m3

Total inside surface area Si of tank ……………………………………………………………..m2

Inside surface area of each compartment Si1 ………………., Si2 ………., …………………..m2

Total outside surface area Se of tank ………………………………………………………….. m2

Mean surface area of tank:S  =  Si.Se …………………………………………………….. m2

Specifications of the tank walls: 4/ 	…………………………………………………………………

Structural peculiarities of the tank: 5/ 	………………………………………………………………….

Number, dimensions and description of manholes ……………………………………………..

……………………………………………………………………………………………………

Description of manhole covers……..……………………………………………………………

…………………………………………………………………………………………………….

Number, dimensions and description of discharge piping……………………………………….

…………………………………………………………………………………..………………

Number and description of tank cradles ………………………………………..………………

…………………………………………………………………………………..………………

Accessories…….………………………………………………………………………………………

……………………………………………………………………………………………………

1/	Delete as necessary (experts only in the case of tests carried out under ATP annex 1, appendix 2, sections 5 or 6).

2/	Wagon, lorry, trailer, semi-trailer, container, etc.

3/	State source of information.

4/	Nature and thickness of materials constituting the tank walls, from the interior to the exterior, mode of construction, etc.

5/	If there are surface irregularities, show how Si and Se were determined.

MODEL No. 2 A

Section 2

Measurement in accordance with ATP, annex 1, appendix 2, sub-section 2.1, of the overall coefficient of heat transfer of equipment other than tanks for liquid foodstuffs

Testing method: inside cooling/inside heating 1/

Date and time of closure of equipment's doors and other openings: ………………………………….….

Averages obtained for ……………	 hours of continuous operation

(from 		……………. a.m./p.m. to ………	 a.m./p.m.):

(a)	Mean outside temperature of body: 	Te = . . . . . . . . . . .  °C ± ……………………….…K

(b)	Mean inside temperature of body: 	Ti =  . . . . . . . . . . . . °C ± ………………………...K

(c)	Mean temperature difference achieved: ΔT = …………………………………………....K

Maximum temperature spread:

Outside body …………………………………………………………………………………….K

Inside body 	……………………………………………………………………………………...K

Mean temperature of walls of bodyTe +Ti2  ……………………………………………………...°C

Operating temperature of heat exchanger 2/ 	  ………………………………………………………..°C

Dew point of atmosphere outside body during continuous operation 2/

………………………………………………. °C ± ……………………………………………………K

Total duration of test …………………………………………………………………………………….h

Duration of continuous operation………………………………………………………………………..h

Power consumed in exchangers: W1 …………………………………………………………………W

Power absorbed by fans: W2 ………………………………………………………………………….W

Overall coefficient of heat transfer calculated by the formula:

Inside-cooling test 1/  	K  =  W1  −W2S .ΔT

Inside-heating test 1/  	K  =  W1 + W2S .ΔT

K =……………………….	W/m2.K

MODEL No. 2 A (cont'd)

Maximum error of measurement with test used ……………………………………………………….%

Remarks: 3/ 	 ………………………………………………………………………………………………

…………………………………………………………………………………………………………….

(To be completed only if the equipment does not have thermal appliances:)

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark IN/IR 1/.

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a) only for a period of not more than six years, that is until ……………………………………………………………………………………………………………

Done at:	…………………………………..

on		…………………………………..	…………………………………..

Testing Officer

l/	Delete as necessary.

2/	For inside-cooling test only.

3/	If the body is not parallelepipedic, specify the points at which the outside and inside temperatures were measured.

MODEL No. 2 B

Section 2

Measurement, in accordance with ATP annex 1, appendix 2, sub-section 2.2, of the overall coefficient of heat transfer of tanks for liquid foodstuffs

Testing method: inside heating

Date and time of closure of equipment's openings………………………………………………………..

Mean values obtained for ……………………………………………...	 hours of continuous operation

(from 		…………a.m./p.m. to …………….	a.m./p.m.):

(a)	Mean outside temperature of tank: Te = ……………	C ± ………………………….K

(b)	Mean inside temperature of tank:

Ti=Sin.TinSin				= …………..	°C± ……………………….K

(c)	Mean temperature difference achieved: ΔT  ……………………………………………..K

Maximum temperature spread:

Inside tank ………………………………………………………………………………………K

Inside each compartment ………………………………………………………………………..K

Outside tank ……………………………………………………………………………………..K

Mean temperature of tank walls ………………………………………………………………………°C

Total duration of test ……………………………………………………………………………………h

Duration of continuous operation ………………………………………………………………………h

Power consumed in exchangers: W1 …………………………………………………………………W

Power absorbed by fans: W2 …………………………………………………………………………W

Overall coefficient of heat transfer calculated by the formula:

K  =  W1 + W2S .ΔT

K = ………….	 W/m2.K

MODEL No. 2 B (cont'd)

Maximum error of measurement with test used ………………………………………………………..%

Remarks: 1/ ……………………………………………………………………………………………....

…………………………………………………………………………………………………………….

(To be completed only if the equipment does not have thermal appliances:)

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark IN/IR. 2/

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a) only for a period of not more than six years, that is until ……………………………………………………………………………………………………………

Done at:………………………………..	………………………………….

on:	………………………………………	Testing Officer

l/	If the tank is not parallelepipedic, specify the points at which the outside and inside temperatures were measured.

2/	Delete as necessary.

MODEL No. 3

Section 2

Expert field check of the insulating capacity of equipment in service in accordance with ATP annex 1, appendix 2, section 5

The check was based on test report No……………………	dated ……………………………….…

issued by approved testing station expert (name and address)	………………………………………..

…………………………………………………………………………………………………………….

Condition when checked:

Top……………………………………………………………………………………………………

Side walls ………………………………………………………………………………………………

End wall………………………………………………………………………………………………

Bottom …………………………………………………………………………………………………

Doors and openings ……………………………………………………………………………………

Seals 	…………………………………………………………………………………………………

Cleaning drainholes ……………………………………………………………………………………

Air tightness	 	……………………………………………………………………………………

………………………………………………………………………………………………………..

K coefficient of the equipment when new (as shown in the previous test report) ……………………

………………………………………………………………………………………………… W/m2.K

Remarks: ………………………………………………………………………………………………

………………………………………………………………………………………………………..

According to the above test results the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for not more than three years, with the distinguishing mark IN/IR. 1/

Done at	………………………………………..

on:	………………………………………..	……………………………..

Testing Officer

1/	Delete as necessary.

MODEL No. 4 A

Section 3

Determination of the efficiency of cooling appliances of refrigerated equipment using ice or dry ice by an approved testing station in accordance with ATP annex 1, appendix 2, sub-section 3.1,

except 3.1.3 (b) and 3.1.3 (c)

Cooling appliance:

Description of cooling appliance …………………………………………………………………..

Nature of refrigerant ………………………………………………………………………………

Nominal refrigerant filling capacity specified

by manufacturer ……………………………………………………………………………….kg

Actual filling of refrigerant used for test ………………………………………………………kg

Drive independent/dependent/mains-operated 1/ …………………………………………………..

Cooling appliance removable/not removable 1/ ……………………………………………………

Manufacturer ………………………………………………………………………………………

Type, serial number ………………………………………………………………………………..

Year of manufacture ……………………………………………………………………………..

Filling device (description, where situated;

attach drawing if necessary) ………………………………………………………………………

……………………………………………………………………………………………………...

Inside ventilation appliances:

Description (number of appliances, etc.) …………………………………………………………..

Power of electric fans …………………………………………………………………………..W

Delivery rate ………………………………………………………………….……..……m3/h

Dimensions of ducts:  cross-section …………	m2, length …………………………….m

Air intake screen; description 1/ ……………………………………………………………………

1/	Delete if not applicable.

MODEL No. 4 A (cont'd)

Automatic devices 	………………………………………………………………………………………..

Mean temperatures at beginning of test:

Inside ………………………………...		°C ± …………………………………………….K

Outside ……………………………….	°C ± …………………………………………….K

Dew point in test chamber ……………	°C ± ………………………………………………K

Power of internal heating system ………………………………………………………………………W

Date and time of closure of equipment's doors and other openings ……………………………..…..

Record of mean inside and outside temperatures of body and/or curve showing variation

of these temperatures with time

……………………………………………………………………………………………………..

Remarks: …………………………………………………………………………………………………

……………………………………………………………………………………………………………..

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ……………………………………………………………………………………

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a) only for a period of not more than six years, that is until ………………….

Done at:	……………………………………….

on:	……………………………………….	………………………………..

Testing Officer

MODEL No. 4 B

Section 3

Determination of the efficiency of cooling appliances of refrigerated equipment with eutectic plates

by an approved testing station in accordance with ATP annex 1, appendix 2, sub-section 3.1,

except 3.1.3 (a) and 3.1.3 (c)

Cooling appliance:

Description 	………………………………………………………………………………………..

Nature of eutectic solution …………………………………………………………………………

Nominal eutectic solution filling capacity specified

by manufacturer ………………………………………………………………………………. kg

Latent heat at freezing temperature stated by manufacturer …………kJ/kg  at ………………°C

Cooling appliance removable/not removable 1/

Drive independent/dependent/mains-operated 1/

Manufacturer …………………………………………………………………………………….

Type, serial number ……………………………………………………………………………….

Year of manufacture ………………………………………………………………………………

Eutectic plates:  Make ………………………..	 Type ……………………………………….

Dimensions and number of plates, where situated;

distance from walls (attach drawing) ………………………………………………………………

…………………………………………………………………………………………………….

Total cold reserve stated by manufacturer for freezing

temperature of ……………………..	kJ  to 	…………………………………………………°C

Inside ventilation appliances (if any):

Description 	 ……………………………………………………………………………………..

Automatic devices 	……………………………………………………………………….………..

l/	Delete if not applicable.

MODEL No. 4 B (cont'd)

Mechanical refrigerator (if any):

Make 	…………………………………	Type 	………………….	 No. …………………

Where situated ……………………………………………………………………………………

Compressor:  Make …………………..	Type 	……………………………………………….

Type of drive …………………………………………………………………………………….

Nature of refrigerant ……………………………………………………………………………

Condenser ………………………………………………………………………………………….

Refrigerating capacity stated by the manufacturer for the specified freezing temperature and an outside temperature of + 30 °C	……………………….………………………………………W

Automatic devices:

Make	 ………………………………	Type ………………………………………….……….

Defrosting (if any) ……………………………………………………………………………….

Thermostat ……………………………………………………………………………………….

LP pressostat ………………………………………………………………………………………

HP pressostat ………………………………………………………………………………………

Relief valve ………………………………………………………………………………………..

Others	……………………………………………………………………………………….

Accessory devices:

Electrical heating devices of the door joint:

Capacity by linear metre of the resistor …………………………………………………….W/m

Linear length of the resistor ……………………………………………………………………m

Mean temperatures at beginning of test:

Inside ……………………………	°C ± …………………………………………………..K

Outside ……………………………	°C ± …………………………………………………….K

Dew point in test chamber …………	°C ± ……………………………………………………K

MODEL No. 4 B (cont'd)

Power of internal heating system ……………………………………………………………………..W

Date and time of closure of equipment's

doors and openings ……………………………………………………………………………………..

Period of accumulation of cold …………………………………………………………………………h

Record of mean inside and outside temperatures of body

and/or curve showing variation of these temperatures

with time ………………………………………………………………………………………………..

………………………………………………………………………………………………………….

Remarks: …………………………………………………………………………………………………..

……………………………………………………………………………………………………………

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ……………………………………………………………………………………….

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a) only for a period of not more than six years, that is until …………………..

Done at:	……………………………………………...

on:	……………………………………………...	……………………………….

Testing Officer

MODEL No. 4 C

Section 3

Determination of the efficiency of cooling appliances of refrigerated equipment using liquefied gases by an approved testing station in accordance with ATP annex l, appendix 2, sub-section 3.1,

except 3.1.3 (a) and 3.1.3 (b)

Cooling appliance:

Description

…………………………………………………………………………………………………...

Drive independent/dependent/mains-operated 1/

Cooling appliance removable/not removable 1/

Manufacturer ……………………………………………………………………………………

Type, serial number …………………………………………………………………………….

Year of manufacture ……………………………………………………………………………

Nature of refrigerant ……………………………………………………………………………

Nominal refrigerant filling capacity specified

by manufacturer ………………………………………………………………………………kg

Actual filling of refrigerant used for test ………………………………………………………..kg

Description of tank	 ………………………………………………………………………………

Filling device (description, where situated) ………………………………………………………

Inside ventilation appliances:

Description (number, etc.) ………………………………………………………….	……….

Power of electric fans …………………………………………………………………………………..W

Delivery rate …………………………………………………………………………………m3/h

Dimensions of ducts:  cross-section ………...…….	m2, length …………………………………m

Automatic devices 	………………………………………………………………………………………..

l/	Delete if not applicable.

MODEL No. 4 C (cont'd)

Mean temperatures at beginning of test:

Inside	 ………………………..……….	°C ± ………………………………………………K

Outside ……………………………….	°C ± ………………………………………………K

Dew point in test chamber ……………	°C ± ………………………………………………K

Power of internal heating system ………………………………………………………………………W

Date and time of closure of equipment's

doors and openings ……………………………………………………………………………………….

Record of mean inside and outside temperatures of body and/or curve showing

variation of these temperatures with time ………………………………………………………………..

…………………………………………………………………………………………………………….

Remarks:…………………………………………………………………………………………………

……………………………………………………………………………………………….…………….

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ……………………………………………………………………………………….

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a), only for a period of not more than six years, that is until ………………….

Done at:	…………………………………………….

on:	…………………………………………….	…………………………………

Testing Officer

MODEL No. 5

Section 3

Determination of the efficiency of cooling appliances of mechanically refrigerated equipment

by an approved testing station in accordance with ATP annex 1,

appendix 2, sub-section 3.2

Mechanical refrigerating appliances:

Drive independent/dependent/mains-operated 1/

Mechanical refrigerating appliances removable/not removable 1/

Manufacturer …………………………………………………………………………………….

Type, serial number ………………………………………………………………………………..

Year of manufacture ……………………………………………………………………………….

Nature of refrigerant and filling capacity ………………………………………………………..

Effective refrigerating capacity stated by manufacturer for an outside temperature of + 30 °C

and an inside temperature of:

0 °C	………………………………………………………………………………….. W

-10 °C	…………………………………………………………………………….W

-20 °C	………………………………………………………………………………W

Compressor:

Make	 …………………………………	Type ……………………………………………….

Drive: electric/thermal/hydraulic 1/

Description ………………………………………………………………………………………….

Make ………………	Type …………..	power …………..	kW …	at …………….rpm

Condenser and evaporator ………………………………………………………………………

Motor element of fan(s):  make ……………	type ……………..	number ………………………

power	 …………………………………	kW	at………………………………………rpm

1/	Delete if not applicable.

MODEL No. 5 (cont'd)

Inside ventilation appliances:

Description (number of appliances, etc.) ………………………………………………………….

Power of electric fans ………………………………………………………………………W

Delivery rate ………………………………………………………………………………….m3/h

Dimensions of ducts:  cross-section ……………	m2, length …………………………………m

Automatic devices:

Make ………………………………………	   Type …………………………………………

Defrosting (if any) ……………………………………………………………………………….

Thermostat ………………………………………………………………………………………

LP pressostat …………………………………………………………………………………….

HP pressostat ……………………………………………………………………………………

Relief valve ………………………………………………………………………………………

Others	………………………………………………………………………………………

Mean temperatures at beginning of test:

Inside temperature …………………		°C ± ……………………………………………K

Outside temperature ……………….		°C ± …………………………………………….K

Dew point in test chamber ………….		°C ± ………………………………………….…K

Power of internal heating system ……………………………………………………………………..W

Date and time of closure of equipment's

doors and other openings …………………………………………………………………………………

Record of mean inside and outside temperatures of body and/or curve showing variation

of these temperatures with time …………………………………………………………………………..

…………………………………………………………………………………………………………

MODEL No. 5 (cont'd)

Time between beginning of test and attainment

of prescribed mean inside temperature of body ……………………………………………………….h

Remarks: ………………………………………………………………………………………………..

……………………………………………………………………………………………………………..

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ………………………………………………………………………………………

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a), only for a period of not more than six years, that is until ……………………..

Done at:	……………………………….

on:	……………………………….	……………………………………

Testing Officer

MODEL No. 6

Section 3

Determination of the efficiency of heating appliances of heated equipment by an approved testing station in accordance with ATP annex 1, appendix 2, sub-section 3.3

Heating appliance:

Description …………………………………………………………………………………………..

Drive independent/dependent/mains-operated 1/

Heating appliance removable/not removable 1/

Manufacturer …………………………………………………………………………………………

Type, serial number ……………………………………………………………………………….

Year of manufacture ……………………………………………………………………………….

Where situated ……………………………………………………………………………………..

Overall area of heat exchange surfaces ………………………………………………………..m2

Effective power rating as specified by manufacturer ………………………………………..kW

Inside ventilation appliances:

Description (number of appliances, etc.) ………………………………………………………...

Power of electric fans ………………………………………………………………………….W

Delivery rate ………………………………………………………………………………….m3/h

Dimensions of ducts:  cross-section ……………….	 m2, length …………………………m

Mean temperatures at beginning of test:

Inside temperature 	………………………………	°C ± ………………………………......K

Outside temperature …………………………….	°C ± …………………………………..K

Date and time of closure of equipment's

doors and other openings ………………………………………………………………………………

1/	Delete if not applicable.

MODEL No. 6 (cont'd)

Record of mean inside and outside temperatures of body and/or

curve showing variation of these temperatures with time ………………………………………………..

………………………………………………………………………………………………….………….

Time between beginning of test and attainment of prescribed

mean inside temperature of body ………………………………………………………………………..h

Where applicable, mean heating output during test to

maintain prescribed temperature difference 2/ between

inside and outside of body ……………………………………………………………………………..W

Remarks: ………………………………………………………………………………………………….

…………………………………………………………………………………………………………….

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than six years, with the distinguishing mark ……………………………………………………………………………………

However, this report shall be valid as a certificate of type approval within the meaning of ATP annex 1, appendix 1, paragraph 6 (a), only for a period of not more than six years, that is until ………………

Done at:	………………………………………….

on:	………………………………………….	………………………………..

Testing Officer

2/	Increased by 35% for new equipment.

MODEL No. 7

Section 3

Expert field check of the efficiency of cooling appliances of refrigerated equipment in service in accordance with ATP annex 1, appendix 2, sub-section 6.1

The check was conducted on the basis of report No………………………………………………………

dated …………………………………………………………………………….,  issued by approved testing station/expert (name, address) …………………………………………………………………….

…………………………………………………………………………………………………………….

Cooling appliance:

Description ………………………………………………………………………………………

Manufacturer …………………………………………………………………………………….

Type, serial number ………………………………………………………………………….….

Year of manufacture …………………………………………………………………………….

Nature of refrigerant ………………………………………………………………………………

Nominal refrigerant filling capacity

specified by manufacturer ……………………………………………………………………...kg

Actual filling of refrigerant used for test ………………………………………………………..kg

Filling device (description, where situated) ……………………………………………………….

Inside ventilation appliances:

Description (number of appliances, etc.) …………………………………………………………

Power of electric fans ………………………………………………………………………….W

Delivery rate ………………………………………………………………………………..m3/h

Dimensions of ducts:  cross-section ……………	 m2, length ………………………………..m

Condition of cooling appliance and ventilation appliances ………………………………………

……………………………………………………………………………………………………

……………………………………………………………………………………………………

Inside temperature attained …………………………………………………………………...°C

At an outside temperature of ……………………………………………………………………°C

MODEL No. 7 (cont'd)

Inside temperature of the equipment before the refrigerating appliance is started …………………….°C

Total running time of the refrigerating unit ……………………………………………………………..h

Time between beginning of test and attainment of prescribed

mean inside temperature of body ………………………………………………………………………. h

Check on operation of thermostat ……………………………………………………………………….

For refrigerated equipment with eutectic plates:

Period of operation of the cooling appliance for freezing

of the eutectic solution ………………………………………………………………………………….h

Period during which inside air temperature is maintained

after the appliance is switched off ……………………………………………………………………..h

Remarks: …………………………………………………………………………………………….

…………………………………………………………………………………………………………….

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than three years, with the distinguishing mark ……………………………………………………………………………………

Done at:	……………………………………………

on:	……………………………………………	……………………………..

Testing Officer

MODEL No. 8

Section 3

Expert field check of the efficiency of cooling appliances of mechanically refrigerated equipment in service in accordance with ATP annex 1, appendix 2, sub-section 6.2

The check was conducted on the basis of report No………………	 dated ………………………….

issued by approved testing station/expert (name, address) ……………………………………………….

…………………………………………………………………………………………………………….

Mechanical refrigerating appliances:

Manufacturer ………………………………………………………………………………………

Type, serial number ………………………………………………………………………………..

Year of manufacture ……………………………………………………………………………….

Description ………………………………………………………………………………………

Effective refrigerating capacity specified by manufacturer for an outside temperature of +30 °C  and an inside temperature of

0 °C 	………………………………………………………………………………W

- 10 °C 	…………………………………………………………………………….W

- 20 °C 	………………………………………………………………………………W

Nature of refrigerant and filling capacity …………………………………………………………….kg

Inside ventilation appliances:

Description (number of appliances, etc.) ………………………………………………………….

Power of electric fans …………………………………………………………………………W

Delivery rate ……………………………………………………………………	……..m3/h

Dimensions of ducts: cross-section  ………………	 m2, length ………………………………..m

Condition of mechanical refrigerating appliance and inside ventilation appliances …………….

……………………………………………………………………………………………………..

MODEL No. 8 (cont'd)

Inside temperature attained …………………………………………………………………………….°C

At an outside temperature of …………………………………………………………………..°C

and with a relative running time of ……………………………………………………………%

Running time …………………………………………………………………………………… h

Check on operation of thermostat ………………………………………………………………………

Remarks: ……………………………………………………………………………………………….

……………………………………………………………………………………………………………..

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3 valid for a period of not more than three years, with the distinguishing mark ………………………………………………………………………………………

Done at:	……………………………………….

on:	…………………………………..……	…………………………….

Testing Officer

MODEL No. 9

Section 3

Expert field check of the efficiency of heating appliances of heated equipment in service in accordance with ATP annex 1, appendix 2, sub-section 6.3

The check was conducted on the basis of report No. ………………..	 dated ………………………….

issued by approved testing station/expert (name, address) ……………………………………………..

…………………………………………………………………………………………………………..

Mode of heating:

Description ………………………………………………………………………………………

Manufacturer …………………………………………………………………………………….

Type, serial number ………………………………………………………………………………

Year of manufacture ……………………………………………………………………………….

Where situated …………………………………………………………………………………….

Overall area of heat exchange surfaces	 ……………………………………………………….m2

Effective power rating as specified by manufacturer ………………………………………….kW

Inside ventilation appliances:

Description (number of appliances, etc.) ……………………………………………………….

Power of electric fans ………………………………………………………………………….W

Delivery rate ………………………………………………………………………………..m3/h

Dimensions of ducts: cross-section ……………………	 m2, length …………………………… m

Condition of heating appliance and inside ventilation appliances ……………………………………….

……………………………………………………………………………………………………………..

…………………………………………………………………………………………………………….

Inside temperature attained …………………………………………………………………………..°C

MODEL No. 9 (cont'd)

At an outside temperature of ………………………………………………………………….°C

and with a relative running time of …………………………………………………….………..%

Running time ……………………………………………………………………………………..h

Check on operation of thermostat ………………………………………………………………………..

Remarks: ………………………………………………………………………………………………….

…………………………………………………………………………………………………………….

According to the above test results, the equipment may be recognized by means of a certificate in accordance with ATP annex 1, appendix 3, valid for a period of not more than three years, with the distinguishing mark ………………………………………………………………………………………

Done at:	……………………………………

on:	……………………………………	………………………………..

Testing Officer

MODEL No. 10

TEST REPORT

prepared in conformity with the provisions of the Agreement on the International Carriage of Perishable Foodstuffs and on the Special Equipment to be Used for such Carriage (ATP)

Test Report No……………

Determination of the effective refrigerating capacity of a refrigeration unit

in accordance with section 4 of ATP annex 1, appendix 2

Approved testing station

Name: ………………………………………………………………………………………………….….

Address: …………………………………………………………………………………………………..

Refrigeration unit presented by: ……………………………………………………………………...

………………………………………………………………………………………………………...

…………………………………………………………………………………………………………

(a)	Technical specifications of the unit

Date of manufacture: ……………………………………	 Make:  …………………………………….

Type:  ………………………………………………	 Serial No: …………………………………..

Category 1/

Self-contained/not self-contained

Removable/not removable

Single unit/assembled components

Description:………………………………………………………………………………………………

……………………………………………………………………………………………………………..

……………………………………………………………………………………………………………

Compressor:		Make: …………………………….		Type: …………………………………

Number of cylinders: …………….		Cubic capacity: …………………….

Nominal speed of rotation: ……………………………………………….……. rpm

Methods of drive 1/:  electric motor, separate internal combustion engine,

vehicle engine, vehicle motion

Compressor drive motor:  (See footnotes 1 and 2)

Electrical:		Make: ………………………		Type: …………………………………….

Power: ……………………..	kW 	at ……………………………………rpm

Supply voltage …………….	 V	Supply frequency ……………………Hz

MODEL No. 10 (cont’d)

Internal combustion engine:	Make: ………………………..		Type: …………………………

Number of cylinders: …………		Cubic capacity: ………………..

Power:………………………	kW 	 at ………………………….rpm					Fuel: ………………………..

Hydraulic motor:			Make:………………………….		 Type: ………………………….

Method of drive: ………………

Alternator:				Make: …………………………		  Type: ………………………..

Speed of rotation: .			(nominal speed given by the manufacturer:

(

(…………………………………………………………………….rpm

(

(minimum speed:  ………………………………………………….rpm

Refrigerant fluid:	………………………………………………………………………………………..

| Heat exchangers |  | Condenser | Evaporator |
| --- | --- | --- | --- |
| Make-type |  |  |  |
| Number of tubes |  |  |  |
| Fan pitch (mm)2/ |  |  |  |
| Tube: nature and diameter (mm)2/ |  |  |  |
| Exchange surface area (m2)2/ |  |  |  |
| Frontal area (m2) |  |  |  |
| FANS | Number |  |  |
|  | Number of blades per fan |  |  |
|  | Diameter (mm) |  |  |
|  | Nominal power (W)2/3/ |  |  |
|  | Total nominal output at a pressure of . . . . . . Pa (m3/h)2/ |  |  |
|  | Method of drive |  |  |

Expansion valve:	Make: …………………………..	 Model: ……………………………………

Adjustable: 1/ …………………..	 Not adjustable: 1/	…………………………..

Defrosting device: ……………………………………………………………………………………….

Automatic device:  …………………………………………………………………………………….

ECE/TRANS/WP.11/218/Add.1

page 52

MODEL No.10 (cont’d)

Results of measurements and refrigerating performance

(Mean temperature of the air to the inlet(s) of the refrigeration unit . . . . . °C)

| Speed of Rotation |  |  |  | Power of internal fan heater | Power absorbed by the unit cooler fan 4/ | Fuel or electrical power consumption | Mean temperature around the body | Internal temperature |  | Effective refrigerating capacity |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Fans 3/ | Alternator 3/ | Compressor 3/ |  |  |  |  | Mean | Inlet to evaporator |  |
|  | rpm | rpm | rpm | W | W | W or l/hr | °C | °C | °C | W |
| Nominal | ....................…..………...………...………….. | ....................…..………...………...…………. | .....................…………..………..………….. | ....................................................…..……… | ........................................................... | .........................................................………. | ....................................................................…... | ............................……..…………… | .........................……..…...………… | ......................................................................... |
| Minimal | .....................….………...………..………….. | ....................…….……..……..….………….. | .....................….………...…….….…………... | ...............................................….....…….……. | ........................................................… | ...................................................................... | ...................................................................... | ..........................…..……....……..… | ...............…....………..…..………… | ........................................................................... |

MODEL No. 10 (cont’d)

(b)	Test method and results:

Test method 1/:  heat balance method/enthalpy difference method

In a calorimeter box of mean surface area = ………………………………………………….. m2

measured value of the U-coefficient of a box fitted with a refrigeration unit:……. W/°C,

at a mean wall temperature of …………………..°C.

In an item of transport equipment:

measured value of the U-coefficient of an item of transport equipment fitted with a refrigeration unit: …………………………………………………………………..W/°C, at a mean wall temperature of ………………………………………………………….°C.

Method employed for the correction of the U-coefficient of the body as a function of the mean wall temperature of the body: ………………………………………………………………………………….

…………………………………………………………………………………………………………….

………………………………………………………………………………………………………….

Maximum errors of determination of:

U-coefficient of the body ……………………………………………………………………….

refrigerating capacity of the unit ………………………………………………………………..

(c)	Checks

Temperature regulator:  Setting ………………..	 Differential ……………………………..°C

Functioning of the defrosting device 1/:  satisfactory/unsatisfactory

Air flow volume leaving the evaporator: 	value measured ………………………………..m3/h

at a pressure of …………………………………Pa

Existence of a means of supplying heat to the evaporator for setting the thermostat between 0 and 12 °C 1/:  	yes/no

(d)	Remarks

…………………………………………………………………………………………………….

………………………………………………………………………………………………………

……………………………………………………………………………………………………..

Done at:	……………………………………

On: 	……………………………………	…………………………

Testing Officer

1/	Delete where applicable.

2/	Value indicated by the manufacturer.

3/	Where applicable.

4/	Enthalpy difference method only.

Annex 1, Appendix 3

A. 	Model form of certificate of compliance of the equipment, as prescribed in annex 1, appendix 1, paragraph 3

FORM OF CERTIFICATE FOR INSULATED, REFRIGERATED, MECHANICALLY

REFRIGERATED OR HEATED EQUIPMENT USED FOR THE INTERNATIONAL

CARRIAGE OF PERISHABLE FOODSTUFFS BY LAND

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / EQUIPMENT 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2 |  |  |  | XXXXXXXXX 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | INSULATED |  |  |  |  |  |  |  |  |  |  |  |  | REFRIGERATED |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MECHANICALLY REFRIGERATED |  |  |  |  |  |  |  |  | HEATED |  |  |  |  |  |  |  |  |  |  |  | MULTI-TEMPERATURE 4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / CERTIFICATE 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ATP XXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Issued pursuant to the Agreement on the International Carriage of Perishable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Foodstuffs and on the Special Equipment to be Used for such Carriage (ATP) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Issuing authority: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Equipment 6: |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. |  |  |  |  |  |  |  |  | / Registration number a: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Vehicle identification number a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / allotted by: |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Insulated box serial number: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Owner or operated by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Submitted by: |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Is approved as: 7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / With one or more thermal appliances which is (are) 1: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.1.1 |  |  |  |  |  |  |  |  | / Independent; 8 |  |  |  |  |  |  |  |  |  |  |  |  |  | MARK, MODEL, FUEL, SERIAL NUMBER/YEAR OF MANUFACTURE (If any) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.1.2 |  |  |  |  |  |  |  |  |  |  |  | / Not independent; 8 |  |  |  |  |  |  |  |  |  |  | MARK, MODEL, FUEL, SERIAL NUMBER/YEAR OF MANUFACTURE (If any) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.1.3 |  |  |  |  |  |  |  |  | / Removable; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.1.4 |  |  |  |  |  |  |  |  |  |  |  | / Not removable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Basis of issue of certificate: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / This certificate is issued on the basis of: 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.1.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Tests of the equipment; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.1.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / conformity with a reference item of equipment; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.1.3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | /A periodic inspection. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Specify: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / The testing station: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / The nature of the tests: 9 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2.3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / The number(s) of the report(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | NNNNNNNN (TESTING STATION) YYYY/MM/DD and NNNNNNNN (TESTING STATION) YYYY/MM/DD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2.4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / The K coefficient: 0,nn W/m2K |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11 |  |  |  |  |  |  |  |  | Nominal capacity |  |  |  |  | Evap.1 |  |  |  |  |  |  |  |  |  |  | Evap.2 |  |  |  |  |  |  | Evap.3 |  |  |
| 7.2.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | °C |  |  |  |  |  |  |  |  | xxxxx W |  |  |  |  | xxxxx W |  |  |  |  |  |  |  |  |  |  | xxxxx W |  |  |  |  |  |  | xxxxx W |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / The effective refrigerating capacity at an |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | °C |  |  |  |  |  |  |  |  | xxxxx W |  |  |  |  | xxxxx W |  |  |  |  |  |  |  |  |  |  | xxxxx W |  |  |  |  |  |  | xxxxx W |  |  |
|  |  |  |  | outside temperature of 30 °C and an inside temperature of: 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | °C |  |  |  |  |  |  |  |  | xxxxx W |  |  |  |  | xxxxx W |  |  |  |  |  |  |  |  |  |  | xxxxx W |  |  |  |  |  |  | xxxxx W |  |  |
| 7.3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Number of openings and special equipment X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.3.1 |  |  |  |  |  |  |  |  |  |  |  |  | / Number of doors: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  | / rear door |  |  |  |  |  |  |  |  |  |  |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / side door(s) X |  |  |  |  |
| 7.3.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Number of vents: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.3.3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Hanging meat equipment: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Others |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / This certificate is valid until: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MONTH & YEAR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.1 |  |  |  |  |  |  |  |  |  |  |  | / Provided that: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.1.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / The insulated body and, |  |  |  |  |  |  |  |  |
|  |  |  |  | where applicable, the thermal appliance is maintained in good condition; and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.1.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / No material alteration is made to the thermal |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | appliances; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9. |  |  |  |  |  |  |  |  |  |  |  |  |  | / Done by: |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CERTIFIED DUPLICATE 12 Do not print this stamp on the original Certificate (Officer name) (Competent or authorized authority) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10. |  |  |  |  |  |  | / On: |  |  |  |  |  |  |  |  |  |  |  |  |  | YYYY/MM/DD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | LOGOTYPE13 Security stamp (relief, ultraviolet, etc.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / The competent authority |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | XXXXXXXXXXXXXXXXXXXXXXXXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 14 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | / Responsible for the ATP |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Original document |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | (Officer name) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a |  |  |  |  |  |  |  | / Not mandatory |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

_____________________

These footnotes shall not be printed on the certificate itself

The areas in grey shall be replaced by the translation in the language of the country issuing the ATP Certificate.

1/ 	Strike out what does not apply.

2 / 	Distinguishing sign of the country, as used in international road traffic.

3/ 	The number (figures, letters, etc.) indicating the authority issuing the certificate and the approval reference.

4/ 	The test procedure is not yet determined within the ATP Agreement. Multi-temperature equipment is insulated equipment with two or more compartments for different temperatures in each compartment.

5/ 	The blank certificate shall be printed in the language of the issuing country and in English, French or Russian; the various items shall be numbered as in the above model.

6/ 	State type (wagon, lorry, trailer, semi-trailer, container, etc.); in the case of tank equipment for carriage of liquid foodstuffs, add the word "tank".

7/ 	Enter here one or more of the descriptions listed in Appendix 4 of Annex 1, together with the corresponding distinguishing mark or marks.

8/ 	Write the mark, model, fuel, serial number and year of manufacture of the equipment.

9/ 	Measurement of the overall coefficient of heat transfer, determination of the efficiency of cooling appliances, etc.

10/ 	Where determined in conformity with the provisions of Appendix 2, paragraph 3.2.7, of this Annex.

11/ 	The effective cooling capacity of each evaporator depends on the number of evaporators fixed at the condensing unit.

12/ 	In case of loss, a new Certificate can be provided or, instead of it, a photocopy of the ATP Certificate bearing a special stamp with “CERTIFIED DUPLICATE” (in red ink) and the name of the certifying officer, his signature, and the name of the competent authority or authorized body.

13/ 	Security stamp (relief, fluorescent, ultraviolet, or other safety mark that certifies the origin of the certificate).

14/ 	If applicable, mention the way the power for issuing ATP Certificates is delegated.

B. 	Certification plate of compliance of the equipment, as provided for in annex 1, appendix 1, paragraph 3

1.		The certification plate shall be affixed to the equipment permanently and in a clearly visible place adjacent to any other approval plate issued for official purposes.  The plate, conforming to the model reproduced below, shall take the form of a rectangular, corrosion-resistant and fire-resistant plate measuring at least 160 mm by 100 mm.  The following particulars shall be indicated legibly and indelibly on the plate in at least the English or French or Russian language:

(a)	the Latin letters "ATP" followed by the words "APPROVED FOR TRANSPORT OF PERISHABLE FOODSTUFFS";

(b)	"APPROVAL NUMBER" followed by the distinguishing sign (in international road traffic) of the State in which the approval was granted and the number (figures, letters, etc.) of the approval reference;

(c)	"EQUIPMENT NUMBER" followed by the individual number assigned to identify the particular item of equipment (which may be the manufacturer's number);

(d)	"ATP MARK" followed by the distinguishing mark prescribed in annex l, appendix 4, corresponding to the class and the category of the equipment;

(e)	"VALID UNTIL" followed by the date (month and year) when the approval of the unit of equipment expires.  If the approval is renewed following a test or inspection, the subsequent date of expiry may be added on the same line.

2.		The letters "ATP" and the letters of the distinguishing mark should be approximately 20 mm high.  Other letters and figures should not be less than 5 mm high.

Annex l, Appendix 4

DISTINGUISHING MARKS TO BE AFFIXED TO SPECIAL EQUIPMENT

The distinguishing marks prescribed in appendix 1, paragraph 4 to this annex shall consist of capital Latin letters in dark blue on a white ground. The height of the letters shall be at least 100 mm for the classification marks and at least 50 mm for the expiry dates. For special equipment, such as a laden vehicle with maximum mass not exceeding 3.5 t, the height of the classification marks could likewise be 50 mm and at least 25 mm for the expiry dates.

The classification and expiry marks shall at least be affixed externally on both sides in the upper corners near the front.

The marks shall be as follows:

Equipment	Distinguishing

mark

Normally insulated equipment	IN

Heavily insulated equipment	IR

Class A refrigerated equipment with normal insulation	RNA

Class A refrigerated equipment with heavy insulation	RRA

Class B refrigerated equipment with heavy insulation	RRB

Class C refrigerated equipment with heavy insulation	RRC

Class D refrigerated equipment with normal insulation	RND

Class D refrigerated equipment with heavy insulation	RRD

Class A mechanically refrigerated equipment with normal

insulation	FNA

Class A mechanically refrigerated equipment with heavy

insulation	FRA

Class B mechanically refrigerated equipment with heavy

insulation	FRB

Class C mechanically refrigerated equipment with heavy

insulation	FRC

Class D mechanically refrigerated equipment with normal

insulation	FND

Class D mechanically refrigerated equipment with heavy

insulation	FRD

Equipment	Distinguishing

mark

Class E mechanically refrigerated equipment with heavy

insulation	FRE

Class F mechanically refrigerated equipment with heavy

insulation	FRF

Class A heated equipment with normal insulation	CNA

Class A heated equipment with heavy insulation	CRA

Class B heated equipment with heavy insulation	CRB

If the equipment is fitted with a removable or non-independent thermal appliance and if special conditions exist for the use of the thermal appliance, the distinguishing mark or marks shall be supplemented by the letter X in the following cases:

1.	FOR REFRIGERATED EQUIPMENT:

Where the eutectic plates have to be placed in another chamber for freezing;

2.	FOR MECHANICALLY REFRIGERATED EQUIPMENT:

2.1	Where the compressor is powered by the vehicle engine;

2.2	Where the refrigeration unit itself or a part is removable, which would prevent its functioning.

The date (month, year) entered under section A, item 8 in appendix 3 of this annex as the date of expiry of the certificate issued in respect of the equipment shall be quoted under the distinguishing mark or marks aforesaid.

Model:

02   =	month (February)	) of expiry of the

2011=	year			) certificate

FRC

0 - 201l

_____________

?/	Wagons, lorries, trailers, semi-trailers, containers and other similar equipment.

?/	In the case of tank equipment, the term "body" means under this definition, the tank itself.

These requirements shall apply to new plates only.  A transitional period of three months shall be granted from the date of entry into force of this requirement.

/     */	To prevent frosting.